## Cassette
			2TR	3TR	4TR	5TR-3P	5TR-1P
Indoor model			MCD-24CR-N	MCD-36CR-N	MCD-48CR-N	MCD-60CR-N	MCD-60CR-N
Indoor unit factory model			PH-KF71Q/Y-D	PH-KF105Q/Y-D	PH-KF140Q/Y-D	PH-KF160Q/Y-D-[N]	PH-KF175Q/Y-D
Indoor code			22022511001356	22022511001396	22022511001376	22022511001436	22022511001416
Outdoor model			MOCA30U-24C-N	MOD30U-36C-N	MOD30U-48C-N	MODU-60C-D	MODU-60C-N
Outdoor unit factory model			PH-KF71W-CA30	PH-KF105W-D30	PH-KF140W-D30	PH-KF175W/S1-590 PH-KF175W/S1-590 PH-KF175W/S1-590	PH-KF175W/590 PH-KF175W/590 PH-KF175W/590
Outdoor code			22022716000775	22022716000795	22022516000502	22022716000815	22022716000835
Power supply		V-ph-Hz	220~230-1-60	220~230-1-60	220~230-1-60	220~230-1-60	220~230-1-60
Cooling	Capacity	Btu/h	24000	36000	47000	60000	60000
	Input	W	2900	4100	5000	6250	6550
	EER	W/W	2.60	2.60	2.75	2.80	2.60
Cooling	Capacity	Kj/h	25320	37980	49585	63300	63300
	Input	W	2900	4100	5000	6250	6550
	EER	Kj/hr	9.4	9.4	9.9	10.1	9.4
Heating	Capacity	Btu/h	/	/	/	/	/
	Input	W	/	/	/	/	/
	COP	W/W	/	/	/	/	/
Indoor fan motor	Model		YKT-42-6-6	YKS-125-6-6	YKS-125-6-6	ZKFN-170-8-1	ZKFN-170-8-1
	Old Model		YDK42-6E	YDK125-6B	YDK125-6B
	Qty		1	1	1	1	1
	Input	w	81/69/63	242/163/144	242/163/144	170(Output)	170(Output)
	Capacitor	uF	3.5UF/450V	4.5UF/450V	4.5UF/450V	/	/
	Speed(hi/mi/lo)	r/min	520/390/340	780/600/550	780/600/550	880/800/720	880/800/720
Indoor coil	a.Number of rows		2	2	3	3	3
	b.Tube pitch(a)x row pitch(b)	mm	21x13.37	21x13.37	21x13.37	21x13.37	21x13.37
	c.Fin spacing	mm	1.4	1.4	1.4	1.4	1.4
	d.Fin type (code)		Hydrophilic aluminium	Hydrophilic aluminium	Hydrophilic aluminium	Hydrophilic aluminium	Hydrophilic aluminium
	e.Tube outside dia.and type	mm	Ф7,Inner grooved tube	Φ7,Inner grooved tube	Φ7,Inner grooved tube	Φ7,Inner grooved tube	Φ7,Inner grooved tube
	f.Coil length x height x width	mm	2010x168x26.74	2010x210x26.76	2080x210x40.11	1930x252x40.11	1930x252x40.11
	g.Number of circuits		8	10	10	10	10
Indoor air flow (Hi/Med/Lo)		m3/hm3/h	1157/1004/829	1851/1346/1232	1854/1362/1240	2204/1988/1770	2281/2060/1842
Sound level (sound pressure)		dB(A)	46/42/39	50/45/43	51/45/44	58/56/54	57/55/53
Throttle type			/	/	/	/	/
Indoor unit	Dimension (W x Dx H)(body)	mm	840x840x205	840x840x245	840x840x245	840x840x287	840x840x287
	Packing (W x Dx H)(body)	mm	900x900x225	900x900x265	900x900x265	900x900x292	900x900x292
	Dimension (W x Dx H)(panel)	mm	950x950x55	950x950x55	950x950x55	950x950x55	950x950x55
	Packing (W x Dx H)(panel)	mm	1035x1035x90	1035x1035x90	1035x1035x90	1035x1035x90	1035x1035x90
	Net/Gross weight(body)	kg	23/26.4	26/30	28/32	31/34	31/34
	Net/Gross weight(panel)	kg	5/8	5/8	5/8	5/8	5/8
Design pressure		MPa	2.6/1.0	2.6/1.0	2.6/1.0	2.6/1.0	2.6/1.0
Drainage water pipe dia.		mm	ODΦ32	ODΦ32	ODΦ32	ODΦ32	ODΦ32
Refrigerant piping	Liquid side/ Gas side	mm	Φ9.52/Φ15.9(3/8"/5/8")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ22(3/8"/7/8")	Φ9.52/Φ22(3/8"/7/8")
Controller			Remote control	Remote control	Remote control	Remote control	Remote control
Operation temperature		℃	17~30	17~30	17~30	17~30	17~30
Room temperature	Cooling	℃	17~32	17~32	17~32	17~32	17~32
	Heating	℃	/	/	/	/	/
Qty’per 20’ /40’ /40'HQ		indoor unit+panel	148/312/342	128/268/294	128/268/294	100/212/238	100/212/238

## Ceiling-Floor
			2TR	3TR	4TR	5TR-3P
Indoor Model			MUE-24CR-N	MUE-36CR-N	MUE-48CR-N	MUE-60CR-N
Indoor unit factory model			PH-KF71DL/Y-E	PH-KF105DL/Y-E	PH-KF140DL/Y-E	PH-KF175DL/Y-E-[N]
Indoor code			22022711001316	22022711001337	22022711001336	22022711001356
Outdoor Model			MOCA30U-24C-N	MOD30U-36C-N	MOD30U-48C-N	MODU-60C-D
Outdoor unit factory model			PH-KF71W-CA30	PH-KF105W-D30	PH-KF140W-D30	PH-KF175W/S1-590 PH-KF175W/S1-590 PH-KF175W/S1-590
Outdoor code			22022716000775	22022716000795	22022516000502	22022716000815
Power supply		V-ph-Hz	220~230-1-60	220~230-1-60	220~230-1-60	220~230-1-60
Cooling	Capacity	Btu/h	24000	36000	48000	60000
	Input	W	2900	4100	5000	6250
	EER	W/W	2.60	2.70	2.75	2.75
Cooling	Capacity	Kj/h	25320	37980	50640	63300
	Input	W	2900	4100	5000	6250
	EER	Kj/hr	9.4	9.7	9.9	9.9
Heating	Capacity	Btu/h	/	/	/	/
	Input	W	/	/	/	/
	COP	W/W	/	/	/	/
Indoor fan motor	Model		YKSS-55-4-9	YKSS-115-4-1	YKSS-85-4-1L	YKSS-130-4-1L
	Old Model		YSK55-4L-2	YSK115-4B	YSK85-4B
	Qty		1		2	2
	Input	W	165/125/95	235/200/172	174/157/144	216/186/171/162 / 216/186/171/162
	Capacitor	uF	2.5UF/450V	5UF/450V	2.5UF/450V	6.5UF/450V
	Speed(Hi/Med/Lo)	r/min	1470/1210/995	1320/1175/1050	1400/1220/1090	1640/1530/1430/1370 / 1640/1530/1430/1370
Indoor coil	Number of rows		2	3	3	4
	Tube pitch(a)x row pitch(b)	mm	21x13.37	21x13.37	21x13.37	21x13.37
	Fin spacing	mm	1.3	1.3	1.3	1.3
	Fin type		Hydrophilic aluminium	Hydrophilic aluminium	Hydrophilic aluminium	Hydrophilic aluminium
	Tube outside dia.and type	mm	Ф7,Inner grooved tube	Ф7,Inner grooved tube	Ф7,Inner grooved tube	Ф7,Inner grooved tube
	Coil length x height x width	mm	795x294x26.74	1010x294x40.11	1300x294x40.11	1375x546x53.48
	Number of circuits		6	5	8	12
Throttle type			/	/	/	/
Indoor unit	Dimension (WxDxH)	mm	1068x675x235	1285x675x235	1650x675x235	1650x675x235
	Packing (WxDxH)	mm	1145x755x313	1360x755x313	1725x755x313	1725x755x313
	Net/Gross weight	kg	24.7/29.5	32/37	40/45.5	45.5/51.5
Design pressure		MPa	2.6/1.0	2.6/1.0	2.6/1.0	2.6/1.0
Drainage water pipe diameter		mm	ODΦ25	ODΦ25	ODΦ25	ODΦ25
Refrigerant piping	Liquid side/Gas side	mm(inch)	Φ9.52/Φ15.9(3/8"/5/8")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ22(3/8"/7/8")
Controller			Remote control	Remote control	Remote control	Remote control
Operation temperature		℃	17~30	17~30	17~30	17~30
Room temperature	Cooling	℃	17~32	17~32	17~32	17~32
	Heating	℃	/	/	/	/
Qty’per 20’ /40’ /40'HQ (indoor unit)			102/220/252	92/188/213	72/147/167	72/147/167

## Duct
			2TR	3TR	4TR	5TR-3P
Indoor model			MTB-24CW-N	MTB-36CW-N	MTB-48CW-N	MTB-60CW-N
Indoor unit factory model			PH-KF71T2/X-B	PH-KF105T2/X-B	PH-KF140T2/X-B	PH-KF175T2/X-B
Indoor code			22023011002134	22023011002174	22023011002154	22023011002194
Outdoor model			MOCA30U-24C-N	MOD30U-36C-N	MOD30U-48C-N	MODU-60C-D
Outdoor unit factory model			PH-KF71W-CA30	PH-KF105W-D30	PH-KF140W-D30	PH-KF175W/S1-590 PH-KF175W/S1-590 PH-KF175W/S1-590
Outdoor code			22022716000775	22022716000795	22022516000502	22022716000815
Power supply		V-ph-Hz	220~230-1-60	220~230-1-60	220~230-1-60	220~230-1-60
Cooling	Capacity	Btu/h	24000	36000	47000	60000
	Input	W	2900	4100	5000	6250
	EER	W/W	2.80	2.65	2.80	2.75
Cooling	Capacity	Kj/h	25320	37980	49585	63300
	Input	W	2900	4100	5000	6250
	EER	Kj/hr	10.1	9.5	10.1	9.9
Heating	Capacity	Btu/h	/	/	/	/
	Input	W	/	/	/	/
	COP	W/W	/	/	/	/
Indoor fan motor	Model		YKSS-74-6-2	YKSS-140-6-2	YKSS-170-6-10	YKSS-170-6-10
	Old Model		YSK74-6PB	YSK140-6B	YSK170-6B	YSK170-6B
	Qty		1	1	1	1
	Input	W	139/112/100	235/195/173	303/230/193	303/230/193
	Capacitor	uF	3.5UF/450V	10UF/450V	10UF/450V	10UF/450V
	Speed(Hi/Med/Lo)	r/min	875/730/670	1060/910/820	1080/880/760	1080/880/760
Indoor coil	Number of rows		4	4	4	4
	Tube pitch(a)*row pitch(b)	mm	21x13.37	21x13.37	21x13.37	21x13.37
	Fin spacing	mm	1.5	1.5	1.5	1.5
	Fin type		Hydrophilic aluminium	Hydrophilic aluminium	Hydrophilic aluminium	Hydrophilic aluminium
	Tube outside dia.and type	mm	Φ7,Inner grooved tube	Φ7,Inner grooved tube	Φ7,Inner grooved tube	Φ7,Inner grooved tube
	Coil length×height×width	mm	733x252x53.48	955x336x53.48	1030x378x53.48	1030x378x53.48
	Number of circuits		6	8	8	8
Indoor air flow (Hi/Med/Lo) Indoor air flow (Hi/Med/Lo)		m3/hm3/h	1107/886/797	1629/1478/1303	2176/1790/1531	2281/1869/1618
ESP	Rated	Pa	25	37	50	50
	Range	Pa	0-80	0-80	0-100	0-120
Indoor noise level (Hi/Med/Lo)		dB(A)	40.2/36.8/35.5	48.3/45.7/43.5	56/51.7/49.2	50.2/46.9/44.5
Throttle type			/	/	/	/
Indoor unit	Dimension (WxDxH)	mm	920x635x270	1140x775x270	1200x865x300	1200x865x300
	Packing(WxDxH)	mm	1150x655x350	1355x795x350	1405x920x373	1405x920x373
	Net/Gross weight	kg	28.5/33.5	42/47	46.1/54.4	49/55
Design pressure		MPa	2.6/1.0	2.6/1.0	2.6/1.0	2.6/1.0
Drainage water pipe diameter		mm	ODΦ25	ODΦ25	ODΦ25	ODΦ25
Refrigerant piping	Liquid side/ Gas side	mm	Φ9.52/Φ15.9(3/8"/5/8")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ22(3/8"/7/8")
Controller			Wired control	Wired control	Wired control	Wired control
Operation temperature		℃	17~30	17~30	17~30	17~30
Room temperature	Cooling	℃	17~32	17~32	17~32	17~32
	Heating	℃	/	/	/	/
Qty’per 20’ /40’ /40'HQ		Indoor	108/216/252	75/153/170	60/126/147	60/126/147

## Floor-Standing
			3TR	5TR
Code			22022210000971	22022210001111
Factory model			PH-KF105LW/Y-JJ2	PH-KF160LW/S1Y-EE2(B4)-W			J2 Type				E type
Indoor code			22022211000987	22022211001127
Indoor unit factory model			PH-KF105L/Y-JJ2	PH-KF160L/S1Y-EE2(B4)-W
Outdoor code			22022716000795	22022216000447
Outdoor unit factory model			PH-KF105W-D30	PH-KF160W/S1-543VL(B4)-W
Model			MFJ-36CR-N	MFE-60CR-DB4W
Indoor			MFJ-36CR-N	MFE-60CR-DB4W
Outdoor			MOD30U-36C-N	MOVL-60C-DB4W
Power supply		V-ph-Hz	220~230-1-60	220-3-60
Cooling	Capacity	Btu/h	36000	60000
	Input	W	4100	6100
	Rated current	A	20	18.5
	EER	W/W	2.65	2.80
Cooling	Capacity	Kj/h	37980	63300
	Input	W	4100	6100
	Rated current	A	20	18.5
	EER	Kj/hr	9.5	10.4
Heating	Capacity	Btu/h	----	----
	Input	W	----	----
	Rated current	A	----	----
	COP	W/W	----	----
Max. input consumption		W	5400	7800
Max. current		A	26	24.5
Starting current		A	101	137
Compressor	Model		LHT53NBAC	ZR57KE-TF5-52E
	Type		ROTARY	SCROLL
	Brand		MITSUBISHI	Copeland
	Capacity	Btu/h	38385	57500
	Input	W	3660	4960
	Rated current(RLA)	A	17.6	12.3
	Locked rotor Amp(LRA)	A	101	137
	Thermal protector		-----	----
	Thermal protector position		INTERNAL	----
	Capacitor	uF	65UF/450V	----
	Refrigerant oil/oil charge	ml	ATMOS NM56EP/900	1360
Indoor fan motor	Model		YKS-120-8-13	YKS-160-8-3-1
	Old Model		YDK120-8B	YDK160-8B1
	Input	W	330/310/280	407/322
	Capacitor	uF	6.5	8
	Speed(Hi/Mi/Lo)or (Hi/Lo)	r/min	590 / 540 / 470	595/480
Indoor coil	a.Number of rows		2	3
	b.Tube pitch(a)x row pitch(b)	mm	25.4x22	25.4x22
	c.Fin spacing	mm	1.3	1.5
	d.Fin type (code)		Hydrophilic aluminium	Hydrophilic aluminium
	e.Tube outside dia.and type	mm	Φ9.52,innergroove tube	Φ9.52,innergroove tube
	f.Coil length x height x width	mm	422x965x26.74	485x813x66
	g.Number of circuits		6	6
Indoor air flow(Hi/Mi/Lo)or (Hi/Lo)		m3/h	1785/1560	2400/2300/2000
Indoor noise level(Hi/Mi/Lo)or (Hi/Lo)		dB(A)	53.2/48.8	55.6/52.1/49.1
Indoor unit	Dimension(W*D*H)	mm	540x410x1825	606x384x1895
	Packing (W*D*H)	mm	1935x655x555	2025x745x505
	Net/Gross weight	Kg	51/65.4	59.4/71.6
Outdoor fan motor	Model		YKT-60-6-41	YKS-230-6-3L
	Old Model		YDK60-6B	YDK230-6F-1(B)
	Input	W	150/140	310
	Capacitor	uF	4UF/450V	12μF/450V
	Speed	r/min	910/830	1095
Outdoor coil	a.Number of rows		2	1
	b.Tube pitch(a)x row pitch(b)	mm	21x13.37	21×13.37
	c.Fin spacing	mm	1.4	1.3
	d.Fin type (code)		Uhydrophilic aluminium	Unhydrophilic aluminium
	e.Tube outside dia.and type	mm	Φ7, inner grooved tube	Φ7,innergroove tube
	f.Coil length x height x width	mm	1010x756x26.74	2030×798×13.37
	g.Number of circuits		6	5
Outdoor noise level		dB(A)	63.3	64.8
Outdoor unit	Dimension(W*D*H)	mm	946x410x810	710x710x843
	Packing (W*D*H)	mm	1090x500x865	738x738x872
	Net/Gross weight	Kg	60/70	71/76.2
Refrigerant type		g	R22/2000	R22/2700
Design pressure		MPa	2.6/1.0	2.6/1.0
Refrigerant piping	Liquid side/ Gas side	mm(inch)	Φ9.52/Φ19(3/8"/3/4")	Φ12.7/Φ22(1/2"/7/8")
	Max. refrigerant pipe length	m	30	30
	Max. difference in level	m	20	20
Connection wiring			4x1.5(Optional)	- -
Plug type			- -	- -
Thermostat type			Remote Control	Remote Control
Operation temperature		℃℃	17-30	17-30
Room temperature	Indoor(cooling/ heating)	℃℃	17-32/---	17-32/----
	Outdoor(cooling/heating)	℃	18-43/---	18-52/----
Application area		m2	48-70	77-113
Qty’per 20’ /40’ /40'HQ			21/44/56	21/46/54

## Outdoor
			2TR	3TR	4TR	5TR-3P	5TR-1P
Model			MOCA30U-24C-N	MOD30U-36C-N	MOD30U-48C-N	MODU-60C-D	MODU-60C-D
Factory model			PH-KF71W-CA30	PH-KF105W-D30	PH-KF140W-D30	PH-KF175W/S1-590 PH-KF175W/S1-590 PH-KF175W/S1-590	PH-KF175W/S1-590 PH-KF175W/S1-590 PH-KF175W/S1-590
Code			22022716000775	22022716000795	22022516000502	22022716000815	22022716000815
Power supply		V-ph-Hz	220~230-1-60	220~230-1-60	220~230-1-60	220~230-3-60	220~230-3-60
Max. input consumption		W	3750	5400	6500	7800	7800
Max. input current		A	22	26	29	28	28
Compressor	Model		PH370G2C-3MTU	LHT53NBAC	C-SBR145H16A	C-SB373H6A	C-SB373H6A
	Type		ROTARY	ROTARY	SCROLL	Scroll	Scroll
	Brand		GMCC	MITSUBISHI	PANASONIC	SANYO	SANYO
	Capacity	Btu/h		38385	49474	61757/61757	61757/61757
	Input	W		3660	4550	5450/5550	5450/5550
	Rated current(RLA)	A		17.6	21.6	17.3/17.5	17.3/17.5
	Locked rotor Amp(LRA)	A		101	155	134	134
	Thermal protector position			INTERNAL	INTERNAL	INTERNAL	INTERNAL
	Capacitor	μF	55UF/450V	65UF/450V	50UF/450V	/	/
	Refrigerant oil	ml		ATMOS NM56EP/900	1400	SAY56T/1700	SAY56T/1700
Outdoor fan motor	Model		YKT-63-6-200L	YKT-60-6-41	YKS-190-8-1	YKT-65-6-41	YKT-65-6-41
	Old Model			YDK60-6B	YDK190-8B	YDK65-6FB	YDK65-6FB
	Qty		1	1	1	2	2
	Input	W	136/130	150/140	258	164	164
	Capacitor	μF	3UF/450V	4UF/450V	10UF/450V	3.5UF/450V	3.5UF/450V
	Speed	r/min	930/-/830	910/830	810	815	815
Outdoor coil	Number of rows		2	2	2	3	3
	Tube pitch(a)* row pitch(b)	mm	19.5x11.6	21x13.37	21x13.37	21x13.37	21x13.37
	Fin spacing	mm	1.2	1.4	1.4	1.4	1.4
	Fin type		Unhydrophilic aluminium	Uhydrophilic aluminium	Uhydrophilic aluminium	Unhydrophilic aluminium	Unhydrophilic aluminium
	Tube outside dia.and type	mm	Ф5, innergroove tube	Φ7, inner grooved tube	Φ7, inner grooved tube	Ф7, innergroove tube	Ф7, innergroove tube
	Coil length * height * width	mm	768x663x23.2	1010x756x26.74	1010x756x26.74	840x1113x40.11	840x1113x40.11
	Number of circuits		2	6	6	4	4
Outdoor noise level (sound pressure)		dB(A)	61.2	63.3	65.2	62.6	62.6
Throttle type			Throttle valve	Throttle valve	Throttle valve	Throttle valve	Throttle valve
Outdoor unit	Dimension(WxDxH)	mm	845x360x607	946x410x810	946x410x810	900x350x1170	900x350x1170
	Packing(WxDxH)	mm	965x395x755	1090x500x865	1090x500x865	1032x443x1307	1032x443x1307
	Net/Gross weight	kg	42.1/45.4	65.4/71.1	82/87.5	91.5/103	91.5/103
Refrigerant type/Quantity	Type		R22	R22	R22	R22	R22
	Charged volume	kg	1.4	2	2.1	2.95	2.95
Design pressure		MPa	2.6/1.0	2.6/1.0	2.6/1.0	2.6/1.0	2.6/1.0
Refrigerant piping	Liquid side/ Gas side	mm(inch)	Φ9.52/Φ15.9(3/8"/5/8")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ19(3/8"/3/4")	Φ9.52/Φ22(3/8"/7/8")	Φ9.52/Φ22(3/8"/7/8")
	Max. pipe length	m	30	30	30	30	30
	Max. difference in level	m	10	20	20	20	20
Ambient temperature	Cooling	℃	18-43	18-43	18-43	18-43	18-43
	Heating	℃	-7-24	-7-24	-7-24	-7-24	-7-24
Qty’per 20’ /40’ /40'HQ		Outdoor unit	102/216/216	44/96/144	44/96/144	27/57/108	27/57/108