## Cassette
项目号			2TR	3TR
Indoor model			MCD-24CRDN1-N	MCD-36CRDN1-N
Indoor unit factory model			PH-KF71Q/BP2N1Y-D	PH-KF105Q4/BP2N1Y-D
Indoor code			22022511000976	22022511000936
Outdoor model			MOCA02U-24CDN1-N	MOD02U-36CDN1-N
Outdoor unit factory model			PH-KF71W/BP2T1N1-CA02	PH-KF105W/BP2T1N1-D02
Outdoor code			22023016000831	22022216000287
Power supply		V-ph-Hz	220~230-1-60	220~230-1-60
Cooling	Capacity	Btu/h	24000	36000
	Input	W	2321	3676
	Current	A	10.1	16.0
	EER	W/W	3.2	3.01
Cooling	Capacity	Kj/h	25320	37980
	Input	W	2321	3676
	Current	A	10.1	16.0
	EER	Kj/hr	11.52	10.836
Heating	Capacity	Btu/h	/	/
	Input	W	/	/
	Current	A	/	/
	COP	W/W	/	/
Indoor fan motor	Model		YKT-42-6-6	YKS-125-6-6
	Old Model		YDK42-6E	YDK125-6B
	Qty		1	1
	Input	w	81/69/63	242/163/144
	Capacitor	uF	2UF/400-450V	4.5UF/450V
	Speed(hi/mi/lo)	r/min	520/390/340	780/600/550
Indoor coil	a.Number of rows		2	2
	b.Tube pitch(a)x row pitch(b)	mm	21x13.37	21x13.37
	c.Fin spacing	mm	1.4	1.4
	d.Fin type (code)		Hydrophilic aluminium	Hydrophilic aluminium
	e.Tube outside dia.and type	mm	Φ7,inner grooved tube	Φ7,inner grooved tube
	f.Coil length x height x width	mm	2010x168x26.74	2010x210x26.74
	g.Number of circuits		8	10
Indoor air flow (Hi/Med/Lo)		m3/hm3/h	1150/1000/850	2000/1700/1450
Sound level (sound pressure)		dB(A)	48/41/38	56/50/48
Throttle type			/	/
Indoor unit	Dimension (W x Dx H)(body)	mm	840x840x205	840x840x245
	Packing (W x Dx H)(body)	mm	900x900x225	900x900x265
	Dimension (W x Dx H)(panel)	mm	950x950x55	950x950x55
	Packing (W x Dx H)(panel)	mm	1035x1035x90	1035x1035x90
	Net/Gross weight(body)	kg	21.5/25	25/30
	Net/Gross weight(panel)	kg	5/8	5/8
Design pressure		MPa	4.2/1.5	4.2/1.5
Drainage water pipe dia.		mm	ODΦ32	ODΦ32
Refrigerant piping	Liquid side/ Gas side	mm	Φ9.52/Φ15.9(3/8"/5/8")	Φ9.52/Φ15.9(3/8"/5/8")
Controller			Remote control	Remote control
Operation temperature		℃	17~30	17~30
Room temperature	Cooling	℃	17~32	17~32
	Heating	℃	/	/
Qty’per 20’ /40’ /40'HQ		indoor unit+panel	148/312/342	128/268/294

## Ceiling Floor
项目号			2TR	3TR
Indoor Model			MUE-24CRDN1-N	MUE-36CRDN1-N
Indoor unit factory model			PH-KF71DL/BP2N1Y-E	PH-KF105DL/BP2N1Y-E
Indoor code			22022711000976	22022711000876
Outdoor Model			MOCA02U-24CDN1-N	MOD02U-36CDN1-N
Outdoor unit factory model			PH-KF71W/BP2T1N1-CA02	PH-KF105W/BP2T1N1-D02
Outdoor code			22023016000831	22022216000287
Power supply		V-ph-Hz	220~230-1-60	220~230-1-60
Cooling	Capacity	Btu/h	24000	36000
	Input	W	2284	3553
	EER	W/W	3.2	3.10
Cooling	Capacity	Kj/h	25320	37980
	Input	W	2284	3553
	EER	Kj/hr	11.52	11.16
Heating	Capacity	Btu/h	/	/
	Input	W	/	/
	COP	W/W	/	/
Indoor fan motor	Model		YKSS-55-4-9	YKSS-115-4-1
	Old Model		YSK55-4L-2	YSK115-4B
	Qty		1	1
	Input	W	165/125/95	235/200/172
	Capacitor	uF	2.5UF/450V	5UF/450V
	Speed(Hi/Med/Lo)	r/min	1470/1210/995	1320/1175/1050
Indoor coil	Number of rows		3	3
	Tube pitch(a)x row pitch(b)	mm	21x13.37	21x13.37
	Fin spacing	mm	1.3	1.3
	Fin type		Hydrophilic aluminium	Hydrophilic aluminium
	Tube outside dia.and type	mm	Ф7,Inner grooved tube	Ф7,Inner grooved tube
	Coil length x height x width	mm	795x294x40.11	1010x294x40.11
	Number of circuits		7	5
Indoor air flow(Hi/Med/Lo)		m3/hm3/h	1350/1150/950	1900/1700/1450
Indoor noise level (sound pressure)(Hi/Med/Lo)		dB(A)	53/48/43	57/54/51
Throttle type			/	/
Indoor unit	Dimension (WxDxH)	mm	1068x675x235	1285x675x235
	Packing (WxDxH)	mm	1145x755x313	1360x755x313
	Net/Gross weight	kg	25/30	30/35
Design pressure		MPa	4.2/1.5	4.2/1.5
Drainage water pipe diameter		mm	ODΦ25	ODΦ25
Refrigerant piping	Liquid side/Gas side	mm(inch)	Φ9.52/Φ15.9(3/8"/5/8")	Φ9.52/Φ15.9(3/8"/5/8")
Controller			Remote control	Remote control
Operation temperature		℃	17~30	17~30
Room temperature	Cooling	℃	17~32	17~32
	Heating	℃	/	/
Qty’per 20’ /40’ /40'HQ (indoor unit)			102/220/252	92/188/213

## Duct
项目号			3TR
Indoor model			MTB-36CWDN1-N
Indoor unit factory model			PH-KF105T2/BP2N1X-B
Indoor code			22023011001595
Outdoor model			MOD02U-36CDN1-N
Outdoor unit factory model			PH-KF105W/BP2T1N1-D02
Outdoor code			22022216000287
Power supply		V-ph-Hz	220-230-1-60
Cooling	Capacity	Btu/h	36000
	Input	W	3459
	Current	A	15.15
	EER	W/W	3.10
Cooling	Capacity	Kj/h	37980
	Input	W	3459
	Current	A	15.15
	EER	Kj/hr	11.16
Heating	Capacity	Btu/h	/
	Input	W	/
	Current	A	/
	COP	W/W	/
Indoor fan motor	Model		YKSS-140-6-2
	Old Model		YSK140-6B
	Qty		1
	Input	W	235/195/173
	Capacitor	uF	10UF/450V
	Speed(Hi/Med/Lo)	r/min	1060/910/820
Indoor coil	Number of rows		4
	Tube pitch(a)*row pitch(b)	mm	21x13.37
	Fin spacing	mm	1.5
	Fin type		Hydrophilic aluminium
	Tube outside dia.and type	mm	Φ7,Inner grooved tube
	Coil length * height * width	mm	955x336x53.48
	Number of circuits		8
Indoor air flow (Hi/Med/Lo) (这是标准静压下的实测值)Indoor air flow (Hi/Med/Lo) (这是标准静压下的实测值)		m3/hm3/h	1900/1600/1450
ESP	Rated	Pa	37
	Range	Pa	0-80
Indoor noise level (Hi/Med/Lo)（标准静压下）Indoor noise level (Hi/Med/Lo)（标准静压下）		dB(A)	52/48/46
Throttle type			/
Indoor unit	Dimension (WxDxH)	mm	1140x775x270
	Packing(WxDxH)	mm	1355x795x350
	Net/Gross weight	kg	37/44
Design pressure		MPa	4.2/1.5
Drainage water pipe diameter		mm	ODΦ25
Refrigerant piping	Liquid side/ Gas side	mm	Φ9.52/Φ15.9(3/8"/5/8")
Controller			Wired control
Operation temperature		℃	17~30
Room temperature	Cooling	℃	17~32
	Heating	℃	/
Qty’per 20’ /40’ /40'HQ		Indoor	75/153/170
Remarks:1.The above design and specifications are subject to change without prior notice for product improvement.

## Floor-standing
		项目号	2TR
Code			22022210000471
Factory model			PH-KF105LW/BP2N1Y-GA
Indoor code			22022211000487					GA type
Indoor unit factory model			PH-KF105L/BP2N1Y-GA
Outdoor code			22022216000287
Outdoor unit factory model			PH-KF105W/BP2T1N1-D02
Model			MFGA-36CRDN1-N
Indoor			MFGA-36CRDN1-N
Outdoor			MOD02U-36CDN1-N
Power supply		V-ph-Hz	220-230-1-60
Cooling	Capacity	Btu/h	36000
	Input	W	3276
	Rated current	A	15
	EER	W/W	3.22
Cooling	Capacity	Kj/h	37980
	Input	W	3276
	Rated current	A	15
	EER	Kj/hr	11.59
Heating	Capacity	Btu/h	----
	Input	W	----
	Rated current	A	----
	COP	W/W	----
Max. input consumption		W	4500
Max. current		A	22
Starting current		A	----
Compressor	Model		ATF250D22UMT
	Type		ROTARY
	Brand		GMCC
	Capacity	Btu/h	26085
	Input	W	2080
	Rated current(RLA)	A	9.45
	Locked rotor Amp(LRA)	A	----
	Thermal protector		----
	Thermal protector position		EXTERNAL
	Capacitor	uF	----
	Refrigerant oil/oil charge	ml	POE(VG74)/670
Indoor fan motor	Model		YKS-120-8-5-1
	Old Model		YDK120-8E
	Input	W	400/330
	Capacitor	uF	5
	Speed(Hi/Mi/Lo)or (Hi/Lo)	r/min	650/550
Indoor coil	a.Number of rows		2
	b.Tube pitch(a)x row pitch(b)	mm	25.4x22
	c.Fin spacing	mm	1.3
	d.Fin type (code)		Hydrophilic aluminium
	e.Tube outside dia.and type	mm	Φ9.52,innergroove tube
	f.Coil length x height x width	mm	422x965x44
	g.Number of circuits		6 / 6
Indoor air flow (Hi/Mi/Lo)or (Hi/Lo)		m3/h	1734/-/1632
Indoor noise level (Hi/Mi/Lo)or (Hi/Lo)		dB(A)	58/-/48
Indoor unit	Dimension(W*D*H)	mm	550x350x1800
	Packing (W*D*H)	mm	1910x685x540
	Net/Gross weight	Kg	50/67
Outdoor fan motor	Model		YKT-60-6-41
	Old Model		YDK60-6B
	Input	W	150/140
	Capacitor	uF	4
	Speed	r/min	910/830
Outdoor coil	a.Number of rows		3
	b.Tube pitch(a)x row pitch(b)	mm	21x13.37
	c.Fin spacing	mm	1.4
	d.Fin type (code)		Hydrophilic aluminium
	e.Tube outside dia.and type	mm	Φ7,innergroove tube
	f.Coil length x height x width	mm	1005x756x40.11
	g.Number of circuits		6
Outdoor noise level		dB(A)	62
Outdoor unit	Dimension(W*D*H)	mm	1030x420x810
	Packing (W*D*H)	mm	1090x500x865
	Net/Gross weight	Kg	69/75
Refrigerant type		g	R410A/2800
Design pressure		MPa	4.2/1.5
Refrigerant piping	Liquid side/ Gas side	mm(inch)	Φ9.52/Φ15.9(3/8"/5/8")
	Max. refrigerant pipe length	m	20
	Max. difference in level	m	10
Connection wiring			- -
Plug type			- -
Thermostat type			Remote Control
Operation temperature		℃℃	17-30
Room temperature	Indoor(cooling/ heating)	℃℃	17-32/----
	Outdoor(cooling/heating)	℃	18-52/----
Application area		m2	48-70
Qty’per 20’ /40’ /40'HQ			22/48/54

## Outdoor
项目号			2TR	3TR
Model			MOCA02U-24CDN1-N	MOD02U-36CDN1-N
Factory model			PH-KF71W/BP2T1N1-CA02	PH-KF105W/BP2T1N1-D02
Code			22023016000831	22022216000287
Power supply		V-ph-Hz	220-230-1-60	220-230-1-60
Max. input consumption		W	3000	4500
Max. input current		A	14	22
Compressor	Model		ATF235D22UMT	ATF250D22UMT
	Type		ROTARY	ROTARY
	Brand		GMCC	GMCC
	Capacity	Btu/h	24345	26085
	Input	W	1970	2080
	Rated current(RLA)	A	6.95	9.45
	Locked rotor Amp(LRA)	A	/	/
	Thermal protector position		EXTERNAL	EXTERNAL
	Capacitor	μF	/	/
	Refrigerant oil	ml	POE(VG74)/670	POE(VG74)/670
Outdoor fan motor	Model		YKT-63-6-200L	YKT-60-6-41
	Old Model		YKT-63-6-200L	YDK60-6B
	Qty		1	1
	Input	W	136/130	150/140
	Capacitor	μF	3UF/450V	4
	Speed	r/min	930/-/830	910/830
Outdoor coil	Number of rows		2	3
	Tube pitch(a)* row pitch(b)	mm	19.5x11.6	21x13.37
	Fin spacing	mm	1.2	1.4
	Fin type		Unhydrophilic aluminium	Hydrophilic aluminium
	Tube outside dia.and type	mm	Ф5, inner groove tube	Φ7,innergroove tube
	Coil length * height * width	mm	768x663x23.2	1005x756x40.11
	Number of circuits		2	6
Outdoor noise level (sound pressure)		dB(A)	60	62
Throttle type			Throttle valve	Throttle valve
Outdoor unit	Dimension(WxDxH)	mm	360x607x914	1030x420x810
	Packing(WxDxH)	mm	965x395x755	1090x500x865
	Net/Gross weight	kg	43/46	69/75
Refrigerant type/Quantity	Type		R410A	R410A
	Charged volume	kg	1.1	2.8
Design pressure		MPa	4.2/1.5	4.2/1.5
Refrigerant piping	Liquid side/ Gas side	mm(inch)	Φ9.52/Φ15.9(3/8"/5/8")	Φ9.52/Φ15.9(3/8"/5/8")
	Max. pipe length	m	50	65
	Max. difference in level	m	25	30
Ambient temperature	Cooling	℃	-15-50	-15-50
	Heating	℃	/	/
Qty’per 20’ /40’ /40'HQ		Outdoor unit	102/216/216	44/96/144