9.1 Error Code List

43

Error Code List

| Malfunction Name | Display Method of Indoor Unit (Error Code) | A/C Status |
| --- | --- | --- |
| Indoor ambient temperature sensor is open/ short- circuited | F1 | The unit will stop operation as it reaches the temperature point. During cooling and drying operation, except indoor fan operates, other loads( such as compressor, outdoor fan, 4-way valve) stop operation; During heating operation, the complete unit stops operation. |
| Indoor evaporator temperature sensor is open/ short-circuited | F2 | The unit will stop operation as it reaches the temperature point. During cooling and drying operation, except indoor fan operates, other loads stop operation; During heating operation, the complete unit stops operation. |
| Blocked protection of IDU fan motor | H6 | IDU fan, ODU fan, compressor and electric heat tube stop operation. Horizontal louver stops at the current position. |
| Malfunction protection of jumper cap | C5 | Operation of remote controller or control panel is available, but the unit won't act. |
| Zero-crossing inspection circuit malfunction of the IDU fan motor | U8 | Operation of remote controller or control panel is available, but the unit won't act. |
| High pressure protection | E1 | During cooling and drying operation, except indoor fan operates, all loads stop operation. During heating operation, if it is inverter unit, the complete unit stops; if it is floor standing unit, the complete unit stops and operation of remote controller or controller is unavailable. |
| Communication malfunction | E6 | During cooling operation, compressor stops while indoor fan motor operates. During heating operation , the complete unit stops. |

44

| Overcurrent protection | E5 | During cooling and drying operation, compressor and outdoor fan stop while indoor fan operates. During heating operation, all loads stop. |
| --- | --- | --- |
| Overload malfunction | E8 | The entire unit stops. |
| Overload protection for compressor | H3 | The entire unit stops. |
| Insufficient fluorine protection | F0 | Indoor fan runs according to set fan and other loads will stop. |
| Outdoor condenser temperature sensor is open/shortcircuited | F4 | The unit will stop operation as it reaches the temperature point. During cooling and drying operation, compressor stops and indoor fan operates; During eating operation , the complete unit stops operation. |
| Malfunction of detecting plate(WIFI ) | JF | Loads operate normally, while the unit can't be normally controlled by APP. |
| Anti-freezing protection for evaporator | E2 |  |
| Cold air prevention protection | H1 |  |
| Refrigerant recovery mode | Fo |  |
| Defrosting | Heating indicator off for 0.5s and then blinks for 10s |  |
| Undefined outdoor unit error | oE | Cool: compressor and outdoor fan stops operation, while indoor fan operates; Heat: compressor, outdoor fan and indoor fan stop operation. |
| Cold air prevention protection | E9 |  |

45

9.2 Procedure of Troubleshooting

Procedure of Troubleshooting

    - Indoor unit:

- Malfunction of Temperature Sensor F1, F2

Main detection points:

  - Is the wiring terminal between the temperature sensor and the controller loosened or poorly contacted?

  - Is there short circuit due to trip-over of the parts?

  - Is the temperature sensor broken?

  - Is mainboard broken?

Malfunction diagnosis process:

Start

Is the wiring terminal between the temperature sensor and the controller loosened or poorly contacted?

Yes

Insert the temperature sensor tightly

No

No	Is malfunction

eliminated

Is there short circuit due to trip- over of the parts

Yes

Make the parts upright

No

No	Is malfunction

eliminated

Yes

Is the temperature sensor normal	No

according to the resistance table?

Yes

46

Replace it with a temperature sensor with the same model

Yes

No	Is malfunction

eliminated

Replace the mainboard with the same model.

Yes

End

- Malfunction of Blocked Protection of IDU Fan Motor H6

Main detection points:

  - SmoothlyIs the control terminal of PG motor connected tightly?

  - SmoothlyIs the feedback interface of PG motor connected tightly?

  - The fan motor can't operate?

  - The motor is broken?

  - Detectioncircuit of the mainboard is defined abnormal?

Malfunction diagnosis process:

Start

While power is off stir the blade

with a tool to see whether the	No

blade rotates smoothly

Yes

Tighten the screw; reassemble the blade, motor and shaft bearing rubber base sub-assy to make sure there is no foreign object between them

No	Is malfunction eliminated

Yes

Check if the connection of PG	No

motor feedback terminal is firm

Insert the control terminal of PG motor tightly

Yes

No

Is malfunction eliminated

Yes

Check if the connection of PG	No

motor control terminal is firm

and motor correctly

Reinstall the blade

Yes

No	Is malfunction eliminated

Yes

Turn on the unit again; measure whether the output voltage on control terminal for PG motor is more than 50V within 1 min after the louvers are opened

Yes

Yes

Yes

Is the motor started up

No

Replace PG motor

Measure the voltage of this foot to

neutral wire on the mainboard	No

No	Is malfunction eliminated

Yes

47

Replace the mainboard with the same model

End

- Malfunction of Protection of Jumper Cap C5

Main detection points:

  - Is there jumper cap on the mainboard?

  - Is the jumper cap inserted correctly and tightly?

  - The jumper is broken?

  - The motor is broken?

  - Detection circuit of the mainboard is defined abnormal?

Malfunction diagnosis process:

Start

Appearance of the jumper cap

Is there jumper cap on the mainboard?	No

Assemble the jumper cap with the same model

Yes

No	Is malfunction eliminated

Is the jumper cap inserted correctly	No

and tightly?

Insert the jumper cap tightly

Yes

No	Is malfunction

eliminated

Yes

Replace the jumper cap with the same model

Is malfunction eliminated

Yes

48

Yes

No

Replace the mainboard with the same model

End

49

Malfunction of Zero-crossing Inspection Circuit Malfunction of the IDU Fan Motor U8

Main detection points:

  - Instant energization afte de-energization while the capacitordischarges slowly?

  - The zero-cross detectioncircuit of the mainboard is defined abnormal?

Malfunction diagnosis process:

No

Yes

End

The zero-cross detection circuit of the mainboard is defined abnormal.Replace the mainboard with the same model

The unit returns to normal. Conclusion:U8 is displayed due to power off/on while the

capacitor discharges slowly.

U8 is still displayed

Start

Turn power off for 1minute,the turn back on

- High pressure protection (E1)

Start

Are the display panel and main board connected tightly?

yes

no

Malfunction is eliminated.

yes

Connect the OVC terminal on the main board with the high pressure switch on the complete unit we l

Are the OVC terminal on the main board connected

we l with the high pressure switch on the complete unit?

yes

no	Malfunction is eliminated.

If the wire of high pressure switch is loosened, please

connect the wires according to the circuit diagram. If the high pressure switch is broken or poorly contacted, please replace it.

no

yes

Is the wiring of high pressure switch loosened? Is the high pressure switch broken or poorly contacted?

yes	Malfunction is eliminated.

yes

no

Is the refrigerant superabundant?

no

no

Adjust the volume of refrigerant according to the requirement of the system

yes

no

Malfunction is eliminated.

yes

Is there poor heat exchange? (Including filth blockage of heat exchanger and bad radiating environment );

no

yes	Malfunction is eliminated.

Adjust the unit to improve the heat exchange of unit

no

yes

Is the ambient temperature too high? (If it is a 3-phase unit, high pressure protection may be caused by over current protection due to this)

Decrease the ambient temperature

yes	Malfunction is eliminated.

yes

no	no

Is the supply voltage normal? (If it is a 3-phase unit, high pressure protection may be caused by overcurrent protection due to this)

yes

Are      the      air intake and air discharge at indoor / outdoor heat

exchanger smooth?

yes

The normal fluctuation is within 10% of the rated voltage on the nameplate

no

no

no

Adjust the system to make the air intake and air discharge of indoor and outdoor heat exchangers smooth

no

Malfunction is eliminated.

Malfunction is eliminated.

yes

yes

Is there filth blockage on the filter or on the heat exchanger fins of indoor / outdoor unit?

Remove the blockage.

yes	Malfunction is eliminated.

yes

no

no

Is there blockage inside the pipeline of the system

n

Open the outdoor gas valve and liquid valve completely

no	no

no

Are the gas valve and liquid valve for outdoor unit opened completely?

yes	no

Malfunction is removed.

Malfunction is eliminated.

yes

yes

Is the high pressure signal at high level?

Malfunction is eliminated.

yes

Replace the contro ler

Connect the display panel with the main board we l

no

Remove the blockage inside the pipeline of the system

yes

Check the system further

no

50

yes	no

End

- Overload Protection Compressor H3

Main detection points:

  - Heat exchange of unit is not good? (heat exchanger is dirty and unit radiating environment is bad)

  - Fan motor is not working?

  - Too much load of the system causes high temperature of compressor after working for a long time?

  - Whether high pressure switch is normal?

  - If the refrigerant is leaked?

Malfunction diagnosis process:

Start

Outdoor and indoor heat exchangers are too dirty or the air inlet/outlet is blocked.

Yes

Clean the outdoor and indoor heat exchangers and remove blockage of air inlet/outlet.

Malfunction is eliminated.

Yes

No	No

Fan motor doesn't work at a normal fan speed; fan speed is too low

or the fan doesn't run.

Yes

Check motor and re-install the motor to make it run normally.

Malfunction is eliminated.

Yes

Make compressor run normally.

No	No

Compressor doesn't work normally. Strange noise or leakage occurs.

Temperature of the shell is too high.

Yes

Malfunction is eliminated.

Yes

Remove blockage in the system.

No	No

System is blocked inside

(dirt block, ice block, oil block, Y-valve not fully open).

Yes

Malfunction is eliminated.

Yes

Replace high pressure switch

No	No

Check whether high pressure switch is normal

Yes

Malfunction is eliminated.

Yes

No	No

Check whether the refrigerant is leaking and cause

overheating protection to compressor

Yes

Check the leaking status of refrigerant and charge refrigerant

Malfunction is eliminated.

Yes

51

No

No

Replace a main board of the same model.

End

52

Malfunction of Insufficient fluorine protection F0

Troubleshooting for F0 malfunction

Heat  exchangers  are too dirty or the air inlet/outlet is blocked.

No

Yes

Clean the heat exchangers and remove blockage of air inlet/outlet.

Malfunction is

eliminated.

Yes

No

Compressor doesn't work norma ly. Strange noise or leakage occurs.

Casing is too hot.

Yes

Malfunction is

eliminated.

Yes

No

No

System  is   blocked   inside (dirt block, ice block, oil block, Y-valve no

fu ly open).

Yes

Malfunction is

eliminated.

Yes

No

No

The refrigerant is leaking

Yes

Check the leaking status of refrigerant and charge refrigerant

Malfunction is

eliminated.

Yes

No

No

Replace a main

End

same model.

board with the

Remove blockage in the system

Make compressor run norma ly.

- High Temperature and Overload Protection (AP1 below means control board of outdoor unit) E8

Start

If the outdoor ambient temperature is higher than 53°C?

Yes

Normal protection, please use it after improving the outdoor ambient temperature

Unit restarts norma ly

Yes

No	No

is good?

Improve the radiating environment of unit (clean the heat exchanger and remove surrounding obstacles)

Unit restarts norma ly

Yes

No	No

If the indoor and outdoor fan are running norma ly?

Connect norma ly?

Yes

Adjust the connection

Yes

Yes

Replace outdoor mainboard

Fan capacitor is broken?

No

Motor is broken?

Yes

Yes

Replace fan capacitor

Replace motor

53

No

Replace mainboard

End

54

Malfunction of detecting plate(WIFI) JF

Start

check if the connection wire are correctly connected

Yes

Replace the detecting plate with the same model

Is malfunction eliminated

Replace the mainboard with the same model

No

Yes

The end

  - Outdoor unit:

- Capacity charging malfunction (outdoor unit malfunction) (AP1 below is control board of outdoor unit)

Main detection point:

  - Detect if the voltage of L and N terminal of wiring board is between 210AC-240AC by alternating voltage meter;

  - Is reactor (L) well connected? Is connection wire loosened or pull-out? Is reactor (L) damaged?

Malfunction diagnosis process:

Turn on the unit and wait 1 minute

Use DC voltmeter to measure the voltage on the two ends of electrolytic capacitor

Voltage higher than 200V?

Fault with the

Y		voltage testing circuit on control

panel AP1

Replace the control panel AP1

Measure the AC voltage between        terminal L and and N on wiring

board XT(power supply)

N

Voltage within 210VAC~250VAC?

Y

Shut down the power and repair the power supply to restore the range 210VAC~250VAC

power on and restart the unit

Y

If the fault is eliminated?

N

Shut down the power and wait 20 minutes; or use DC voltmeter to measure the voltage on the two ends of capacitor (test3), until the voltage is lower than 20V

conn	ctor

Check the ection of rea

(Lin the Electrical Wiring Diagram)

If the wiring of reactor Lis normal?

Connect the reactor Laccording to Electrical Wiring Diagram correctly

Re-energize and turn on the unit

Y

If the fault is eliminated?

55

N

Y

Replace the

control	N

panel AP1

End

e After the unit de-

nergized for 20min

If the radiating of outdoor

and indoor unit is we l?

N

If the indoor and outdoor

fan work we l?

N

Anti-high temperature,

overload protection

If the outdoor ambient temperature is

higher than 53 °C?

56

Diagnosis for anti-high temperature, overload protection (AP1 below is control board of outdoor unit)

Normal protection, please use

Y

it after improve the outdoor ambient temperature

N

Y

en radiating of

Improve the

vironment

unit

OFAN is connected we l 2. Test if resistance value of any two terminals is less than 1kΩ with ohmic meter

1. Check if fan terminal

Y

capacitor C1

Replace fan

control board AP1

Replace

outdoorfan

Replace

End

- IPM protection, phase current overcurrent (the control board as below indicates the control board of outdoor unit) H5/P5

Mainly detect:

(1) Compressor COMP terminal (2) voltage of power supply (3) compressor

Turn on the unit after energization

Whether IPM

protection occurs after the unit has

operated for a while?

(4) Refrigerant-charging volume (5) air outlet and air inlet of outdoor/indoor unit Troubleshooting:

N

Check the connection between the control board and the compressor by referring to the electric wiring diagram

Whether

the voltage between terminal L and terminal N of XT is within 210AVC~ 250VAC?

Whether IPM

protection occurs after the unit has

operated for a while?

Correctly connect the wires of compressor according to the electric wiring diagram, and then turn on the unit

Y

Check whether wires

of compressor (UVW) are connected correctly

Check the power supply voltage and

N	make the power voltage resume to the range of 210VAC~250VAC

Y

- Whether the heat exchangers of indoor unit and outdoor unit are

dirty? Whether the radiation is affected because the unit is covered by the objects?

- When indoor fan and outdoor unit are operate normally?

- Whether the system pressure is too high?

- Whether the pressure is because there's too much refrigerant?

Measure the resistance value among three terminals (UVW) of compressor with a resistance measuring meter.

Whether the

resistance value of three terminals are almost the same.

Measure the resistance between three terminals (UVW)

of compressor and the copper pipe with resistance measuring meter

Whether the resistance value is more than

500ohm?

Whether there's

abnormal phenomenons	Y

described as above?

N

Correct it one by one according to the Service Manual, and then turn on the unit.

N	Replace the compressor

Y

57

Whether the unit

can operate normally?

N

Y

Replace control

board	Y

End

58

Start-up failure (following AP1 for outdoor unit control board)

Mainly detect:

  - Whether the compressor wiring is connected correct?

  - Is compressor broken?

  - Is time for compressor stopping enough?

Fault diagnosis process:

Power on the unit

Is stop time of the compressor longer than 3 minutes?

No

Restart it up after 3 minutes

Yes

Does startup fail?

Yes

Are the wires for the compressor connected correctly? Is connection sequence right?

No	Connect the wires as per the connection

diagram

Yes

Replace the control panel AP1

No

If the fault is eliminated?

No

Replace the compressor

Yes

End

59

Out of step diagnosis for the compressor (AP1 hereinafter refers to the control board of the outdoor unit)

Mainly detect:

  - Is the system pressure too high?

  - Is the input voltage too low?

Fault diagnosis process:

Out of step occurs once the unit is powered on.

Out of step occurs in operation

No

Is stop time of the

c	an

ompressor longer th

3 minutes?

Is the outdoor fan working norma ly?

No

Check if the fan terminal	Replace the fan

OFAN is connected correctly

capacitor C1

Yes

Yes

Are the wires for the compressor connected correctly? Is connection sequence right?

Is the connection made in clockwise direction?

No

Is the outdoor unit blocked Yes by foreign objects?

No

Replace the control panel AP1

Remove foreign objects

Replace the outdoor fan

Connect the wires correctly

Yes

Replace the control panel AP1

If the fault is eliminated?

Yes

Yes  If the fault is eliminated?

No

No

Replace the compressor

Replace the compressor

End

End

60

Overload and air exhaust malfunction diagnosis (following AP1 for outdoor unit control board)

Mainly detect:

  - Is the PMV connected well or not? Is PMV damaged?

  - Is refrigerant leaked?

Fault diagnosis process:

20 minutes after the complete unit is powered off

Is the terminal FA for the electronic expansion valve connected correctly?

No

Connect the wires correctly

Yes

Resistances between the first four pins close to the terminal hole and the fifth pin are almost the same, less than 100 ohm.

Replace the electronic expansion valve

If the fault is eliminated?

Yes

No

Replace the control panel AP1

If the fault is eliminated?

Yes

No

Coolant leakage, refi ling the coolant

End

- Communication malfunction: (following AP1 for outdoor unit control board)

Mainly detect:

  - Is there any damage for the indoor unit mainboard communication circuit? Is communication circuit damaged?

  - Detect the indoor and outdoor units connection wire and indoor and outdoor units inside wiring is connect well or not, if is

there any

damage?

Fault diagnosis process:

Start

The AP1 voltage detection circuit is at fault

If the fault is eliminated?

Yes

No

Yes

Check wiring inside of the indoor and outdoor units

Are wires broken?

No

Check the communication circuit of the outdoor unit

Did the equipment operate norma ly before the failure

occurs?

Yes

No

Check the wiring of the indoor and outdoor units with reference to the

wiring diagram

Is the connection right?

No

No

Correctly connect the corresponding wires for the indoor and outdoor units with reference to

the wiring diagram

If the fault is eliminated?

The communication circuit is abnormal

Yes

Replace the main board AP1 of the outdoor unit

No

Replace the main board of the indoor unit

If the fault is eliminated?

No

Yes

61

Yes

End

Yes

- Malfunction of Overcurrent Protection

Main detection points:

  - Is the supply voltage unstable with big fluctuation?

  - Is the supply voltage too low with overload?

  - Hardware trouble?

Malfunction diagnosis process:

Start

Is the supply voltage unstable

Yes

Is malfunction eliminated

Yes

of the rated voltage on the nameplate

No	No

Is the supply voltage too low with overload?

Yes

Is malfunction eliminated

Yes

Adjust the supply voltage to maintain it within normal range

No	No

Is  the  indoor  /  outdoor heat exchanger dirty,or are the air inlet and outlet blocked?

No

The fan is abnormal? Fan speed is too low or fan doesnt rotate

Yes

Clean the indoor and outdoor heat exchangers and remove the blockage of air inlet and outlet

No

Check the motor and reinsta l the motor to have the fan run norma ly

Yes

Is malfunction eliminated

Is malfunction eliminated

Yes

Yes

No	No

Replace the mainboard with the same model

Measure  the  current  of  live  wire  on the main board with a clamp ampere	No meter.  Is  the  current  higher  than  the value of the overcurrent protection?

Yes	No

Is malfunction eliminated

Yes

Is there blockage inside the system? (Filth blockage, ice plug, greasy blockage, the cut off valve hasnt been opened completely)

Yes Flush the heat exchangers with high pressure nitrogen

Is malfunction eliminated

Yes

No	No

Is the compressor running abnorma ly? Is there abnormal sound or oil leakage; Is the temperature of the she l too high, etc.?

Yes

Replace the compressor

Is malfunction eliminated

Yes

62

No

with the same model

Replace the mainboard

End

9.3 Troubleshooting for Normal Malfunction

63

Troubleshooting for Normal Malfunction

- Air Conditioner Can't be Started Up

| Possible Causes | Discriminating Method (Air conditioner Status) | Troubleshooting |
| --- | --- | --- |
| No power supply, or poor connection for power plug | After energization, operation indicator isn't bright and the buzzer can't give out sound | Confirm whether it's due to power failure. If yes, wait for power recovery. If not, check power supply circuit and make sure the power plug is connected well. |
| Wrong wire connection between indoor unit and outdoor unit, or poor connection for wiring terminals | Under normal power supply circumstances, operation indicator isn't bright after energization | Check the circuit according to circuit diagram and connect wires correctly. Make sure all wiring terminals are connected firmly |
| Electric leakage for air conditioner | After energization, room circuit breaker trips off at once | Make sure the air conditioner is grounded reliably Make sure wires of air conditioner is connected correctly Check the wiring inside air conditioner. Check whether the insulation layer of power cord is damaged; if yes, place the power cord. |
| Model selection for air switch is improper | After energization, air switch trips off | Select proper air switch |
| Malfunction of remote controller | After energization, operation indicator is bright, while no display on remote controller or buttons have no action. | Replace batteries for remote controller Repair or replace remote controller |

- Poor Cooling (Heating) for Air Conditioner

| Possible Causes | Discriminating Method (Air conditioner Status) | Troubleshooting |
| --- | --- | --- |
| Set temperature is improper | Observe the set temperature on remote controller | Adjust the set temperature |
| Rotation speed of the IDU fan motor is set too low | Small wind blow | Set the fan speed at high or medium |
| Filter of indoor unit is blocked | Check the filter to see its blocked | Clean the filter |
| Installation position for indoor unit and outdoor unit is improper | Check whether the installation postion is proper according to installation requirement for air conditioner | Adjust the installation position, and install the rainproof and sunproof for outdoor unit |
| Refrigerant is leaking | Discharged air temperature during cooling is higher than normal discharged wind temperature; Discharged air temperature during heating is lower than normal discharged wind temperature; Units pressure is much lower than regulated range | Find out the leakage causes and deal with it. Add refrigerant. |
| Malfunction of 4-way valve | Blow cold wind during heating | Replace the 4-way valve |
| Malfunction of capillary | Discharged air temperature during cooling is higher than normal discharged wind temperature; Discharged air temperature during heating is lower than normal discharged wind temperature; Unitt pressure is much lower than regulated range. If refrigerant isn't leaking, part of capillary is blocked | Replace the capillary |
| Flow volume of valve is insufficient | The pressure of valves is much lower than that stated in the specification | Open the valve completely |
| Malfunction of horizontal louver | Horizontal louver can't swing | Refer to point 3 of maintenance method for details |
| Malfunction of the IDU fan motor | The IDU fan motor can't operate | Refer to troubleshooting for H6 for maintenance method in details |
| Malfunction of the ODU fan motor | The ODU fan motor can't operate | Refer to point 4 of maintenance method for details |
| Malfunction of compressor | Compressor can't operate | Refer to point 5 of maintenance method for details |

- Horizontal Louver Can't Swing

| Possible Causes | Discriminating Method (Air conditioner Status) | Troubleshooting |
| --- | --- | --- |
| Wrong wire connection, or poor connection | Check the wiring status according to circuit diagram | Connect wires according to wiring diagram to make sure all wiring terminals are connected firmly |
| Stepping motor is damaged | Stepping motor can't operate | Repair or replace stepping motor |
| Main board is damaged | Others are all normal, while horizontal louver can't operate | Replace the main board with the same model |

64

ODU Fan Motor Can't Operate

| Possible causes | Discriminating method (air conditioner status) | Troubleshooting |
| --- | --- | --- |
| Wrong wire connection, or poor connection | Check the wiring status according to circuit diagram | Connect wires according to wiring diagram to make sure all wiring terminals are connected firmly |
| Capacity of the ODU fan motor is damaged | Measure the capacity of fan capacitor with an universal meter and find that the capacity is out of the deviation range indicated on the nameplate of fan capacitor. | Replace the capacity of fan |
| Power voltage is a little low or high | Use universal meter to measure the power supply voltage. The voltage is a little high or low | Suggest to equip with voltage regulator |
| Motor of outdoor unit is damaged | When unit is on, cooling/heating performance is bad and ODU compressor generates a lot of noise and heat. | Change compressor oil and refrigerant. If no better, replace the compressor with a new one |

- Compressor Can't Operate

| Possible causes | Discriminating method (air conditioner status) | Troubleshooting |
| --- | --- | --- |
| Wrong wire connection, or poor connection | Check the wiring status according to circuit diagram | Connect wires according to wiring diagram to make sure all wiring terminals are connected firmly |
| Capacity of compressor is damaged | Measure the capacity of fan capacitor with an universal meter and find that the capacity is out of the deviation range indicated on the nameplate of fan capacitor. | Replace the compressor capacitor |
| Power voltage is a little low or high | Use universal meter to measure the power supply voltage. The voltage is a little high or low | Suggest to equip with voltage regulator |
| Coil of compressor is burnt out | Use universal meter to measure the resistance between compressor terminals and it's 0 | Repair or replace compressor |
| Cylinder of compressor is blocked | Compressor can't operate | Repair or replace compressor |

- Air Conditioner is Leaking

| Possible causes | Discriminating method (air conditioner status) | Troubleshooting |
| --- | --- | --- |
| Drain pipe is blocked | Water leaking from indoor unit | Eliminate the foreign objects inside the drain pipe |
| Drain pipe is broken | Water leaking from drain pipe | Replace drain pipe |
| Wrapping is not tight | Water leaking from the pipe connection place of indoor unit | Wrap it again and bundle it tightly |

- Abnormal Sound and Vibration

| Possible causes | Discriminating method (air conditioner status) | Troubleshooting |
| --- | --- | --- |
| When turn on or turn off the unit, the panel and other parts will expand and theres abnormal sound | Theres the sound of "PAPA" | Normal phenomenon. Abnormal sound will disappear after a few minutes. |
| When turn on or turn off the unit, theres abnormal sound due to flow of refrigerant inside air conditioner | Water-running sound can be heard | Normal phenomenon. Abnormal sound will disappear after a few minutes. |
| Foreign objects inside the indoor unit or therere parts touching together inside the indoor unit | Theres abnormal sound fro indoor unit | Remove foreign objects. Adjust all parts position of indoor unit, tighten screws and stick damping plaster between connected parts |
| Foreign objects inside the outdoor unit or therere parts touching together inside the outdoor unit | Theres abnormal sound fro outdoor unit | Remove foreign objects. Adjust all parts position of outdoor unit, tighten screws and stick damping plaster between connected parts |
| Short circuit inside the magnetic coil | During heating, the way valve has abnormal electromagnetic sound | Replace magnetic coil |
| Abnormal shake of compressor | Outdoor unit gives out abnormal sound | Adjust the support foot mat of compressor, tighten the bolts |
| Abnormal sound inside the compressor | Abnormal sound inside the compressor | If add too much refrigerant during maintenance, please reduce refrigerant properly. Replace compressor for other circumstances. |