## Generator
Building Equipment Maintenance Record Log 2021
Location :		Head office
Name Equipment :		Generator		Manufacturer's contact details :		Cummins
Model :		C300D6		Date Of Purchase :
Serial Number :		EA71803917		Person responsible for equipment :		Sr. Maintenance
Manufacturer :		Cummins		Frequency:		Monthly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/28/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	02/20/21	Operational	General Visual inspection / cleaning / Test run / collect data
02/20/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	04/24/21	Operational	General Visual inspection / cleaning / Test run / collect data
04/28/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	05/28/21	Operational	General Visual inspection / cleaning / Test run / collect data
05/21/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	06/24/21	Operational	General Visual inspection / cleaning / Test run / collect data
06/24/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	07/21/21	Operational	General Visual inspection / cleaning / Test run / collect data
07/21/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	08/20/21	Operational	Discharge Battery due to battery charger dis connected.
08/20/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	09/27/21	Operational	General Visual inspection / cleaning / Test run / collect data Re fill 40 Liters Diesel
09/27/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	10/21/21	Operational	General Visual inspection / cleaning / Test run / collect data Re fill 40 Liters Diesel
10/21/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	11/25/21	Operational	General Visual inspection / cleaning / Test run / collect data Re fill 40 Liters Diesel
11/25/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	12/14/21	Operational	General Visual inspection / cleaning / Test run / collect data Re fill 40 Liters Diesel
12/14/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	01/14/22	Operational	General Visual inspection / cleaning / Test run / collect data

Note:	Equipment in Operational & Good Condition

			Prepared by :	_______________	Noted by:	______________
Equipment Maintenance Record Log 2022	Equipment Maintenance Record Log 2022
Location :		Head office
Name Equipment :		Generator		Manufacturer's contact details :			Cummins
Model :		C300D6		Date Of Purchase :
Serial Number :		EA71803917		Person responsible for equipment :			Sr. Maintenance
Manufacturer :		Cummins		Frequency:		Monthly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/12/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	02/08/22	Operational	General Visual Inspection / cleaning / Test run / collect data Re fill 20 liters of diesel
02/08/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	03/18/22	Operational	General Visual Inspection / cleaning / Test run / collect data Re fill 20 liters of diesel
03/18/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	04/20/22	Operational	General Visual Inspection / cleaning / Test run / collect data Re fill 60 liters of diesel
04/20/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	05/31/22	Operational	General Visual Inspection / cleaning / Test run / Check Battery & add 3 liters battery solution and repaint rusted areas.
05/31/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	06/12/22	Operational	General Visual Inspection / cleaning / Test run / collect data Re fill 40 liters of diesel
06/12/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	07/21/22	Operational	General Visual Inspection / cleaning / Test run / collect data
07/21/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	08/10/22	Operational	General Visual Inspection / cleaning / Test run / collect data Re fill 40 liters of diesel
08/10/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	09/05/22	Operational	General Visual Inspection / cleaning / Test run / collect data
09/05/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	10/05/22	Operational	General Visual Inspection / cleaning / Test run / collect data
10/05/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	11/08/22	Operational	General Visual Inspection / cleaning / Test run / collect data
11/08/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	12/08/22	Operational	General Visual Inspection / cleaning / Test run / collect data
12/08/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	01/09/22	Operational	General Visual Inspection / cleaning / Test run / collect data

Note:	Equipment in Operational & Good Condition
			Prepared by :	_______________	Noted by:	______________

## Fire Pump
Building Equipment Maintenance Record Log 2021
Location :		Head office
Name Equipment :		Fire Pump		Manufacturer's contact details :
Model :		8RH		Date Of Purchase :
Capacity		500 GPM		Person responsible for equipment :		Sr. Maintenance
Manufacturer :		Layne / vertiline		Frequency:		Monthly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
02/16/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A		Operational	General Check up/ Cleaning ( Churn ) testing was conducted
N/A	N/A	N/A	N/A	N/A	N/A	N/A	N/A
N/A	N/A	N/A	N/A	N/A	N/A	N/A	N/A
N/A	N/A	N/A	N/A	N/A	N/A	N/A	N/A
N/A	N/A	N/A	N/A	N/A	N/A	N/A	N/A
07/21/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	08/29/21	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
08/23/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	09/29/21	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
09/29/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	10/27/21	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
10/27/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	11/26/21	Operational	General Check up/ Cleaning ( Free flow ) 15 min. testing was conducted
11/26/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	12/13/21	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
12/13/21	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A		Operational	General Check up/ Cleaning ( Churn ) testing was conducted

Note:	Equipment in Operational & Good Condition

			Prepared by :	_______________	Noted by:	________________

Building Equipment Maintenance Record Log 2022
Location :		Head office
Name Equipment :		Fire Pump		Manufacturer's contact details :
Model :		8RH		Date Of Purchase :
Capacity		500 GPM		Person responsible for equipment :		Sr. Maintenance
Manufacturer :		Layne / vertiline		Frequency:		Monthly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/28/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
02/15/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted GPM Test 480
N/A	N/A	N/A	N/A	N/A	N/A	N/A	N/A
N/A	N/A	N/A	N/A	N/A	N/A	N/A	N/A
05/17/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
06/28/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
07/26/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
08/10/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
09/24/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
10/06/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted
11/09/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Free flow ) 15 min. testing was conducted
12/05/22	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted

Note:	Equipment in Operational & Good Condition

			Prepared by :	_______________	Noted by:	________________

Building Equipment Maintenance Record Log 2023
Location :		Head office
Name Equipment :		Fire Pump		Manufacturer's contact details :
Model :		8RH		Date Of Purchase :
Capacity		500 GPM		Person responsible for equipment :		Sr. Maintenance
Manufacturer :		Layne / vertiline		Frequency:		Monthly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/23/23	P/M Monthly Inspection & Manual Test run	Building Maintenance	N/A	N/A	N/A	Operational	General Check up/ Cleaning ( Churn ) testing was conducted

Note:	Equipment in Operational & Good Condition

			Prepared by :	_______________	Noted by:	________________

## Elevator
Building Equipment Maintenance Record Log 2022
Location :		Head office
Name Equipment :		Elevator		Manufacturer's contact details :
Model :				Date Of Purchase :
Capacity				Person responsible for equipment :		IEEI Personnel
Manufacturer :				Frequency:		Monthly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/27/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked Hoisting rope car top and Pit room, ( OK )
02/23/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked Hoisting rope car top and Pit room, ( OK ) Recommended to Replace Back up Battery ( DM7,12V 17AH
03/22/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked Hoisting rope car top and Pit room, ( OK ) Recommended to Replace Back up Battery ( DM7,12V 17AH
04/27/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked And Cleaned Door Interlocked ( OK ) Recommended to Replace Back up Battery ( DM7,12V 17AH
05/30/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Adjust T ket Stand at 2nd flr. Added oil at oiler fan main and counter weight rail
06/25/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Check , Cleaned , Car rod , Door interlock
06/27/22	Special Service	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	( Defective back up Battery) Replaced four (4) Pcs back up Battery 12 V 7 AH
07//29/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked door inter lock, car top, safety door edge / adjust finger contact.
08/30/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked, Cleaned , car top, door inter lock
09/21/22	Emergency Check Up	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Conduct Emergency check up due to Unusual noise / No found trouble
10/03/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked & Cleaned door Interlock, entrance sill ,Car top, safety door edge and pit area. Added oil at oiler fan main and C.W.T
10/27/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked & Cleaned door Interlock, Safety door edge
11/23/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	General Check up/ Cleaning ( Churn ) testing was conducted

Note:	Equipment in Operational & Good Condition

			Prepared by :	__________________	Noted by:	___________________
Building Equipment Maintenance Record Log 2023
Location :		Head office
Name Equipment :		Elevator		Manufacturer's contact details :
Model :				Date Of Purchase :
Capacity				Person responsible for equipment :		IEEI Personnel
Manufacturer :				Frequency:		Monthly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/27/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked Hoisting rope car top and Pit room, ( OK )
02/23/22	P/M Monthly Inspection & Manual Test run	IEEI Personnel	N/A	Senior Maintenance	N/A	Unit Is in Operation	Checked Hoisting rope car top and Pit room, ( OK )

Note:	Equipment in Operational & Good Condition

			Prepared by :	_______________	Noted by:	________________

## S.T.P
Building Equipment Maintenance Record Log 2020
Location :		Head office
Name Equipment :		Sewage Treatment Plant		Manufacturer's contact details :
Model :		S.B.R type		Date Of Purchase :
Capacity				Person responsible for equipment :		Building Maintenance
Manufacturer :				Frequency:		Quarterly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
11/19/19	Curative Maintenance	Bram's	11/19/23	Senior Maintenance	N/A	Clogged E.Q.T Motor due to Wipes & tissue / Pull out E.Q.T/ pump 1 & repair	Unit Operational
12/11/19	Preventive Maintenance	Building Maintenance	12/11/19	Senior Maintenance	N/A	Conduct preventive Maintenance work Inspect All electrical & mechanical parts	Unit Operational
01/08/20	Curative Maintenance	Bram's	01/08/20	Senior Maintenance	N/A	Main Bar screen Installation	Unit Operational
01/23/20	Preventive Maintenance	Building Maintenance	01/23/20	Senior Maintenance	N/A	Conduct preventive Maintenance work Inspect All electrical & mechanical parts Oil & Belts replace	Unit Operational
03/04/20	Curative Maintenance	Building Maintenance	03/04/20	Senior Maintenance	N/A	Clogged E.Q.T Motors 1&2 Pull out & repair	Unit Operational
07/07/20	Curative Maintenance	Building Maintenance	07/07/20	Senior Maintenance	N/A	Clogged E.Q.T Motor 1 due to Wipes & tissue & Breaker / Relay Replace ( Damage breaker)	Unit Operational
09/02/20	Curative Maintenance	Building Maintenance	09/02/20	Senior Maintenance	N/A	Man hole Cover Pull treads Damage. / Man hole cover Pull handle Fabricate ( S.B.R )	Unit Operational
09/04/20	Curative Maintenance	Building Maintenance	09/04/20	Senior Maintenance	N/A	Man hole Cover Pull treads Damage. / Man hole cover Pull handle Fabricate ( E.Q.T )	Unit Operational
09/18/20	Curative Maintenance	Building Maintenance	09/18/20	Senior Maintenance	N/A	CCT & E.Q.T Pump Malfunction / Pull out motor & Repair	Unit Operational
09/21/20	Curative Maintenance	Bram's	09/21/20	Senior Maintenance	N/A	Panel Indicator light busted	Unit Operational ( No available Light )
10/06/20	Curative Maintenance	Building Maintenance	09/06/20	Senior Maintenance	N/A	Air Blower motor unusual noise./ Replace bearing & Oil seal	Unit Operational
10/12/20	Curative Maintenance	Building Maintenance	10/12/20	Senior Maintenance	N/A	Decanter Pump Motor stock up./ Pull out motor & Repair	Unit Operational

Note:	Equipment in Operational & Good Condition
			Prepared by :	_________________________		Noted by:______________________
Building Equipment Maintenance Record Log 2021
Location :		Head office
Name Equipment :		Sewage Treatment Plant		Manufacturer's contact details :
Model :		S.B.R type		Date Of Purchase :
Capacity				Person responsible for equipment :		Building Maintenance
Manufacturer :				Frequency:		Quarterly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/04/21	Curative Maintenance	Building Maintenance	01/04/21	Senior Maintenance	N/A	Pull Out E.Q.T Pump 1 Clogged / air defusser loose	Unit Operational
04/16/21	Curative Maintenance	Building Maintenance	04/16/21	Senior Maintenance	N/A	Pull out &Repair Chlorine pump Malfunction	Unit Operational
04/28/21	Preventive Maintenance	Building Maintenance	05/21/21	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil / Belts change	Unit Operational
06/01/21	Preventive Maintenance	Building Maintenance	06/25/21	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil	Unit Operational
07/12/21	Preventive Maintenance	Building Maintenance	07/21/21	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing	Unit Operational
11/16/21	Preventive Maintenance	Building Maintenance	11/22/21	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing	Unit Operational
11/23/21	Preventive Maintenance	Building Maintenance	11/22/21	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil	Unit Operational

Note:	Equipment in Operational & Good Condition

			Prepared by :	_________________________		Noted by:______________________

Building Equipment Maintenance Record Log 2022
Location :		Head office
Name Equipment :		Sewage Treatment Plant		Manufacturer's contact details :
Model :		S.B.R type		Date Of Purchase :
Capacity				Person responsible for equipment :		Building Maintenance
Manufacturer :				Frequency:		Quarterly

Date:	Maintenance Description	Maintenance Performed by :	Date Of Validation before put into service	Validation Performed by :	Next maintenance plan on ( date )	Condition	Remarks :
01/10/22	Preventive Maintenance	Building Maintenance	01/10/22	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing	Unit Operational
01/17/22	Preventive Maintenance	Building Maintenance	07/19/22	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil / Belts change	Unit Operational
05/11/22	Curative Maintenance	Building Maintenance	05/11/22	Senior Maintenance	N/A	E.Q.T Pump 1 Not working Pull out Motor & Repair	Unit Operational
07/11/22	Curative Maintenance	Bram's	07/11/22	Senior Maintenance	N/A	E.Q.T Pump 1 & 2 Malfunction / Motor Pull Out & Repair	Unit Operational
07/19/22	Preventive Maintenance	Building Maintenance	07/19/22	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing	Unit Operational
07/21/22	Preventive Maintenance	Building Maintenance	07/21/22	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil / Belts change for Blower	Unit Operational
07/27/23	Preventive Maintenance	Building Maintenance	07/27/23	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil / Belts change for exhaust fan	Unit Operational
09/20/22	Preventive Maintenance	Building Maintenance	09/20/22	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil / Belts change	Unit Operational
11/15/22	Preventive Maintenance	Building Maintenance	11/15/22	Senior Maintenance	N/A	Conduct Preventive maintenance Work schedule / Mechanical Re greasing / Gear oil Replace	Unit Operational

Note:	Equipment in Operational & Good Condition
			Prepared by :	_________________________		Noted by:______________________