“Jockey Pump”

1.	Before starting the jockey pump motor, you should check and do the following;

a. Make sure that no leaks in pipelines, stand pipe and pipe connected to fire hose cabinet.

b. Make sure that the firefighting water tank is always 100% full. (See level switch on water tank actual)

c. Suction strainer should be totally clean and in good condition.

d. Ask permission to Electrical Department to clear out LOTO Permit to work, if any.

e. Make sure that the shaft is freely rotating.

f. Make sure regrease the bearings of pump and motor.

g. Check the pressure switch and local pressure gauge is in working condition.

h. Open the suction valve.

i. Bleed / release the air of the pipeline and pump.

j. Open the discharge valve.

k. Closed re-circulation valve.

2. Inform to energized the main supply of firefighting MCC panel by our Electrical Technician.

3. Turn on the breaker of jockey pump motor on the panel and set to Auto or in Manual mode.

Note: Auto mode means to pressurized only the firefighting pipeline and the motor will stop automatically when the pressure at maximum limit of 12 bars and the motor will run when the pressure at minimum limit of 4 bars. Manual mode means for continuous running of motor, no stopping.

4. Start the jockey pump motor, if unusual sound occurs immediately stop the motor and check the equipment.

Note: While the motor is running the Mechanical Technician should conduct a   walkthrough to all the pipeline on the plant, if leaks occur immediately stop the motor, drain the water on pipes and repair on it.

5.	At auto mode selector switch, if no leaks on the pipeline the motor will stop automatically when the pressure at maximum limit of 12 bars and the motor will run when the pressure at minimum limit of 4 bars.

6.	If the pressure switch not functioning well, open the re-circulation line of jockey pump motor to prevent over pressure of the pipeline and stop the motor immediately. Call the maintenance team to check the pressure switch.