## Blank copy
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS2-FCU 11
SERIAL #: |  | 15331704-10004
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 3rd Floor (Credit & collection)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS

## SYS2-FCU 11
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS2-FCU 11
SERIAL #: |  | 15331704-10004
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 3rd Floor (Credit & collection)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS
2021-01-09 | - | HO-045930 | Not cooling | Replaced PCB indoor | - | DONE-OK
2021-01-16 | - | HO-46826 | Not cooling | Check up / clean drain pod | - | DONE-OK
2021-12-04 | - | HO-089278 | Dirty unit | General cleaning only | Clean filter only | DONE-OK
2022-05-28 | - | HO-109818 | Dirty unit | General cleaning only | Clean filter only | DONE-OK
2023-01-07 | - | HO-135416 | Dirty unit | General cleaning only | Clean filter only | DONE-OK
2023-04-17 | - | HO-148408 | E1 Error code | Remove Jumper cup | For observation | DONE-OK
2023-07-15 | - | HO-152457 | Dirty unit | General cleaning only | Clean filter only | DONE-OK
2023-05-20 | - | HO-152491 | Auto on / off | Re installed Jumper Cap | - | DONE-OK
2023-05-25 | - | HO-154881 | E1 Error code | Check up only | - | DONE-OK
2023-11-29 | - | HO-179708 | L3 Error | Check up only | - | DONE-OK
2023-11-30 | - | HO-180006 | L3 Error | Replace water drain pump/ modified drain line hose | - | DONE-OK
2024-02-17 | - | HO-188150 | Check up | Install circuit breaker / Re wiring | - | DONE-OK
2024-03-16 | - | HO-189498 | Dirty unit | General cleaning only | Clean filter only | DONE-OK
2024-03-23 | - | HO-191998 | Dirty unit | General cleaning only | Clean filter only | DONE-OK
2025-03-01 | # 2069 | HO-243686 | Dirty unit | General cleaning only | Clean filter only | DONE-OK
2025-03-29 | # 2081 | HO-248133 | Foul Odor | Removed anti bacterial filter /wash filter | - | DONE-OK
2025-08-30 | # 1033 | HO-270443 | Dirty unit | General cleaning only | Clean filter only | DONE-OK