## Blank copy
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | FCU 1
SERIAL #: |  | 20131706-10017
MODEL NAME : |  | KLM-SS70-2C1M
LOCATION: |  | 4TH Floor (MS. AMY)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS

## FCU 1
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | FCU 1
SERIAL #: |  | 20131706-10017
MODEL NAME : |  | KLM-SS70-2C1M
LOCATION: |  | 4TH Floor (MS. AMY)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS
2024-01-18 | - | HO-185041 | Water dripping | Replace water drain pump / water level sensor | - | DONE-OK
2024-01-20 | - | HO-185294 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2024-03-03 | - | HO-216012 | Not cooling | Check up /cleaning of drain pump | - | DONE-OK
2024-08-08 | - | HO-216628 | Not cooling | Check up only | For replacement of compressor | DONE-OK
2024-08-19 | - | HO-218779 | Not cooling | Replaced PCB outdoor / Comprtessor leadwire | - | DONE-OK
2024-09-06 | - | HO-221041 | Not cooling | Line Phasing | - | DONE-OK
2024-09-17 | - | HO-222286 | Not cooling | Replaced PCB otdoo | - | DONE-OK
2024-10-28 | - | HO-228217 | Not cooling | Replaced PCB indoor and outdoor | - | DONE-OK
2024-11-15 | - | HO-230594 | Not cooling | Re soldered compressor relay | Clean filter regularly | DONE-OK
2025-01-28 | # 2051 | HO-239939 | Weak cooling | Check up | - | DONE-OK
2025-01-31 | - | HO-240405 | malfunstion of low pressure switch /deffective discharge sensor | Replaced Discharge sensor by pass low pressure switch | - | DONE-OK
2025-05-26 | # 2099 | HO-257869 | Water dripping | Clean drain pad and pump | - | DONE-OK
2025-06-21 | # 1005 | HO-261823 | Water dripping | Check up only / No trouble found | - | DONE-OK
2025-08-11 | # 1027 | HO-268588 | Water dripping / Deffective compressor | Check up | For replacement of compressor / PCB (I) (o) | DONE-OK
2025-08-12 | # 1027 | HO-268700 | Not cooling | Replaced Compressor / PCB outdoor | - | DONE-OK
2025-10-08 | # 1066 | HO-275920 | Water dripping | Re-align unit and replaced water pump / float switch | For observation | DONE-OK
2025-10-11 | # 1069 | HO-276542 | Water dripping | Check up , Removed water at drain pan | - | DONE-OK
2025-10-18 | # 1060 | HO-277306 | Repair | Repaced board and install circuit breaker | - | DONE-OK
2025-11-08 | # 1086 | HO-278363 | Water dripping | Check up | For modification of drain line | DONE-OK
2025-11-15 | # 1086 | HO-279854 | Water dripping | Check up | Need Scalfolding | DONE-OK
2025-11-22 | # 1099 | HO-280783 | Water dripping | Restoration of drain pump hose & fixed circuit breaker | - | DONE-OK