“Procedure for Hydro Diesel Pump Motor”

1.	Before starting the hydro diesel pump motor, you should check and do the following;

a. Make sure that no leaks on pipelines, stand pipe and pipe connected to fire hose cabinet.

b. Make sure that the firefighting water tank is always 100% full. (See level switch on water tank actual)

c. Make sure diesel tank is clean and always maintain the level to 90-95%.

d. Check the two battery and should be in working condition.

e. The radiator coolant is always on normal level.

f. The air filter is always clean and in good condition.

g. Open the suction valve of the diesel.

h. On the panel of hydro diesel pump motor both DC supply and battery charger should be in on condition.

i. The Oil should always be in normal level.

j. The diesel filter is always clean and in good condition.

k. Suction strainer should be totally clean and in good condition.

l. Make sure that the shaft is freely rotating.

m. Make sure regrease the bearings of pump and motor.

n. Check the pressure switch and local pressure gauge is in working condition.

o. Open the suction valve.

p. Bleed / release the air of the pipeline and pump.

q. Open the discharge valve.

r. Open re-circulation valve at 50%.

s. Ask permission to Electrical Department to clear out LOTO Permit to work, if any, and to be ready the hydro diesel panel prior to start the hydro diesel motor.

2. On hydro diesel panel put the selector switch to manual mode.

3. Inform the plant personnel team that ready to start the motor, slowly open the discharge valve and hold the impact of the pressure on hoses.

4. Electrical Technician will give the signal to start the motor and the WTP Operator / Mechanical Technician will adjust the re-circulation / return line to maintain the 12 bars pressure on the pipeline.

5. If the hydro diesel pump already started, please check the hr rpm meter, ammeter, oil pressure gauge, oil temperature and water gauge temperature should be on normal reading or the hand is on green indication.

6.	WTP Operator / Electrical Technician will monitor the level of firefighting water tank.

7.	 If the testing is done or the fire is out, inform Electrical Technician to stop the motor and WTP Operator / Mechanical Technician will close the re-circulation line of the hydro diesel pump motor.

8.	Press the stop red button of hydro diesel pump motor on hydro diesel panel.

9. Put the selector switch to zero on hydro diesel panel which is the standby mode.

10. Refill the diesel tank and always maintain the level to 90-95%.