## Blank copy
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 10
SERIAL #: |  | 15331704-10024
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (Marketing)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS

## SYS1-FCU 10
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 10
SERIAL #: |  | 15331704-10024
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (Marketing)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS
2022-01-08 | - | HO-92245 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2022-01-15 | - | HO-92712 | Not cooling / L3 | Replaced drain pump and Float SW | - | DONE-OK
2022-06-25 | - | HO-114559 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2022-07-06 | - | HO-116091 | Weak fan blow / Weak cooling | Check velocity | For GC | DONE-OK
2022-07-08 | - | HO-116322 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-02-04 | - | HO-135449 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-08-12 | - | HO-163271 | Check up | Installation of drain hose | Clean filter regularly | DONE-OK
2024-06-15 | - | HO-197656 | Dirty unit /L3 Error | General cleaning only / REPLACED anti freeze | Clean filter regularly | DONE-OK
2025-02-22 | # 2066 | HO-242887 | No ciccuit breaker | Installation of Circuit breaker | - | DONE-OK
2025-03-01 | # 2069 | HO-243075 | Dirty unit | General cleaning only - 1ST | Clean filter regularly | DONE-OK
2025-10-20 | # 1060 | HO-277305 | Dirty unit / Replacement of Fan motor | General cleaning / replaced fan motor | - | DONE-OK