## Blank copy
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 5
SERIAL #: |  | 15331704-10008
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (Account officer)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS

## SYS1-FCU 5
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 5
SERIAL #: |  | 15331704-10008
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (Account officer)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS
2021-01-30 | - | HO-048626 | Water dripping | Replace drain pump / Water level pump | - | DONE-OK
2021-02-06 | - | HO-49799 | for check up | Replaced indoor board and drain pump | - | DONE-OK
2021-02-20 | - | HO-051737 | L3 ERROR | Replaced drain pump | - | DONE-OK
2021-03-20 | - | HO-55914 | Deffective PCB indoor / Water level | Replace PCB indoor /Water level sensor | - | DONE-OK
2021-03-20 | - | HO-55528 | Not cooling | Adjustment of drain hose drain pump | - | DONE-OK
2021-05-29 | - | HO-64969 | Not cooling / L3 | Replaced drain pump | - | DONE-OK
2022-07-02 | - | HO-115150 | Dirty filter | General cleaning only / Get parameters | Clean filter regularly | DONE-OK
2023-01-28 | - | HO-139049 | Dirty unit | General cleaning only / Test run | Clean filter regularly | DONE-OK
2023-08-12 | - | HO-163270 | Dirty unit | General cleaning only / Test run | Clean filter regularly | DONE-OK
2023-11-25 | - | HO-177277 | Dirty unit | General cleaning only / Test run | Clean filter regularly | DONE-OK
2024-04-27 | - | HO-197655 | Dirty unit | General cleaning only / Test run | Clean filter regularly | DONE-OK
2025-02-08 | # 2060 | HO-241274 | Dirty unit | General cleaning only / Test run | Clean filter regularly | DONE-OK
2025-02-22 | # 2066 | HO-241452 | No circuit breaker | Installation of Circuit breaker / Test run | - | DONE-OK
2025-07-12 | # 1014 | HO-263019 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK