## Blank copy
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 7
SERIAL #: |  | 15331704-10021
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (CSR)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS

## SYS1-FCU 7
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 7
SERIAL #: |  | 15331704-10021
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (CSR)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS
2021-03-20 | - | HO-055101 | Water dripping | Adjustment drain hose drain pump | - | DONE-OK
2022-01-08 | - | HO-92242 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2022-03-23 | - | HO-101096 | Not cooling /L3 error | Replaced drain pump & float valve | - | DONE-OK
2022-05-25 | - | HO-114556 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-01-28 | - | HO-139051 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-04-19 | - | HO-148916 | Not cooling /L3 error | Cleaning of drain pump | Clean filter regularly | DONE-OK
2023-08-19 | - | HO-166734 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-10-16 | - | HO-175054 | D4 Error / not cooling | Replace Sensor Sub assembly | - | DONE-OK
2023-11-18 | - | HO-178747 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2024-06-15 | - | HO-197521 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2024-09-28 | - | HO-223911 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2025-02-15 | # 2062 | HO-242042 | Dirty unit | General cleaning only -1ST | Clean filter regularly | DONE-OK
2025-06-28 | # 1008 | HO-263011 | Dirty unit | General cleaning only - 2ND | Clean filter regularly | DONE-OK
2025-09-13 | # 1043 | HO-272904 | L3 Error | Reset socket connector | - | DONE-OK
2025-09-20 | # 1050 | HO-273252 | L3 Error / repeat GC | General cleaning only | Clean filter regularly | DONE-OK
2025-09-27 | # 1054 | HO-274204 | Deffective water pump / clogged chain hose | Replaced water pump and drain hose | - | DONE-OK