## Blank copy
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 8
SERIAL #: |  | 15331704-10005
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (Sir Adolf)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS

## SYS1-FCU 8
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS1-FCU 8
SERIAL #: |  | 15331704-10005
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 2nd Floor (Sir Adolf)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS
2021-12-11 | - | HO-89925 | Water dripping | General cleaning only | -
2022-01-08 | - | HO-89925 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2022-01-28 | - | HO-94163 | Water dripping | Replaced drain pump | - | DONE-OK
2022-04-27 | - | HO-105286 | L3 Error code | Cleaning of drain pump, Float switch and Flashing of Drain line | - | DONE-OK
2022-05-11 | - | HO-107307 | L3 / not cooling | Check up only/ alignment of indoor unit | - | DONE-OK
2022-05-14 | - | HO-108036 | L3 / not cooling | Drain line converted to Green hose | - | DONE-OK
2022-06-25 | - | HO-114557 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2022-07-06 | - | HO-116095 | Check up | Check velocity and temp | - | DONE-OK
2023-07-29 | - | HO-163265 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-11-18 | - | HO-178750 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2024-04-27 | - | HO-197650 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2024-05-10 | - | HO-223910 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2025-02-15 | # 2026 | HO-242046 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2025-06-28 | # 1008 | HO-263014 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2025-08-05 | # 1021 | HO-269757 | Check up | Transfer master indoor from Sir alvin to Sir Adolf | - | DONE-OK