## Blank copy
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS2-FCU 13
SERIAL #: |  | 15331704-10014
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 3rd Floor (SVC Accounting)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS

## SYS2-FCU 13
AIRCONDITIONTIONG UNIT PREVENTIVE & CURATIVE CARD
INDOOR UNIT #: |  | SYS2-FCU 13
SERIAL #: |  | 15331704-10014
MODEL NAME : |  | VRK5-30CSINV
LOCATION: |  | 3rd Floor (SVC Accounting)
DATE | BWOR # | SERVICE JOB REPORT No. | FINDINGS | REPAIR DONE | RECOMMENDATION | REMARKS
2020-06-27 | - | HO-22889 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2021-01-30 | - | HO-48628 | Weak cooling | Replaced anti freeze | - | DONE-OK
2021-12-24 | - | HO-89303 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2022-04-23 | - | HO-104668 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2022-05-28 | - | HO-109416 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-01-07 | - | HO-135415 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-06-17 | - | HO-152500 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2023-02-17 | - | HO-188103 | Check up | Install circuit breaker | - | DONE-OK
2025-02-01 | # 2053 | HO-240293 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2025-03-29 | # 2081 | HO-248132 | Foul Odor | Removed anti bacterial filter and wash filter | - | DONE-OK
2025-04-12 | # 2086 | HO-250068 | Dirty unit | General cleaning only | Clean filter regularly | DONE-OK
2025-07-18 | # 1016 | HO-265717 | Dead set | Adjustment of remote setting | - | DONE-OK