## AC Monitoring - GC-2025 (hidden)
KOLIN PHILIPPINES INTERNATIONAL INC.
1854 Santa Rita St. Guadalupe Nuevo, Makati City
ACU/AHU PREVENTIVE MAINTENANCE SCHEDULE 2025
|  |  |  | 1st General Cleaning JAN - JUNE |  |  | 2nd General Cleaning JULY - DECEMBER
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS-ACU1(M) | 15401704-10006 | ROOF DECK | ROOF DECK | HO-237287 | 2044 | 2025-01-11 | HO-272849 | 1043 | 2025-09-13
SYS-ACU1A | 15401704-10001 |  | ROOF DECK | HO-237275 | 2044 | 2025-01-11 | HO-272848 | 1043 | 2025-09-13
SYS-ACU1B | 15401704-10005 |  | ROOF DECK | HO-237277 | 2044 | 2025-01-11 | HO-272846 | 1043 | 2025-09-13
SYS-ACU1C | 15401704-10008 |  | ROOF DECK | HO-237274 | 2044 | 2025-01-11 | HO-272844 | 1043 | 2025-09-13
SYS-ACU2(M) | 15401704-10007 |  | ROOF DECK | HO-237279 | 2044 | 2025-01-11 | HO-272854 | 1043 | 2025-09-13
SYS-ACU2A | 15401704-10002 |  | ROOF DECK | HO-237285 | 2044 | 2025-01-11 | HO-272853 | 1043 | 2025-09-13
SYS-ACU2B | 15401704-10004 |  | ROOF DECK | HO-237283 | 2044 | 2025-01-11 | HO-272852 | 1043 | 2025-09-13
SYS-ACU2C | 15401704-10003 |  | ROOF DECK | HO-237280 | 2044 | 2025-01-11 | HO-272850 | 1043 | 2025-09-13
AHU | 15411711-10001 |  | ROOF DECK | HO-237278 | 2044 | 2025-01-11 | HO-272855 | 1043 | 2025-09-13
|  |  | 9 | 9 |  |  | 9
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS1-FCU15 | 15371704-10001 | UPPER GROUND | CLINIC |  |  |  | HO-273318 | 1045 | 2025-09-20
FCU11 | 18071705-14341 |  | TOOLS & PARTS OFFICE | HO-237958 | 2048 | 2025-01-18 | HO-273243 | 1050 | 2025-09-20
FCU12 | 17151706-10195 |  | CUSTOMER LOUNGE | HO-237957 | 2050 | 2025-01-25 | HO-273244 | 1050 | 2025-09-20
SYS1-FCU16 | 15331704-10011 |  | LOBBY AREA | HO-239122 | 2050 | 2025-01-25 | HO-264616 | 1014 | 2025-07-12
SYS1-FCU17 | 15381704-10001 |  | SHOWROOM -HALLWAY | HO-237962 | 2047 | 2025-01-15 | HO-275273 | 1056 | 2025-10-02
SYS1-FCU18 | 15381704-10002 |  | SHOWROOM - LEFT SIDE | HO-237961 | 2047 | 2025-01-15 | HO-275274 | 1056 | 2025-10-02
AIR CURTAIN | 14032210-10023 |  | Reception - Right Side |  |  |  | HO-273734 | 1050 | 2025-09-20
| 14032210-10047 |  | Reception - Left Side |  |  |  | HO-273736 | 1050 | 2025-09-20
AHU |  |  | (UPPER GROUND) - Tech CR |  |  |  | HO-275277 | 1056 | 2025-10-02
|  |  | 9 | 5 |  |  | 9
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS1-FCU1 | 15331704-10010 | 2ND FLOOR | SALES DEPT | HO-240949 | 2060 | 2025-02-08 | HO-277307 | 1060 | 2025-10-25
SYS1-FCU2 | 15331704-10001 |  | SALES DEPT. (MISS MITCH) | HO-241270 | 2066 | 2025-02-08 | HO-275519 | 1060 | 2025-10-25
SYS1-FCU3 | 15341704-10001 |  | SALES DEPT. (SIR KEITH) | HO-237273 | 2044 | 2025-01-11 | HO-267268 | 1025 | 2025-08-07
SYS1-FCU4 | 15361704-10001 |  | SALES DEPT. (MS. JOANA) | HO-241271 | 2060 | 2025-02-08 | HO-263020 | 1014 | 2025-07-12
SYS1-FCU5 | 15331704-10008 |  | ACCOUNT OFFICERS | HO-241274 | 2060 | 2025-02-08 | HO-263019 | 1014 | 2025-07-12
SYS1-FCU6 | 15331704-10007 |  | CSR AREA | HO-242044 | 2062 | 2025-02-15 | HO-263012 | 1008 | 2025-06-28
SYS1-FCU7 | 15331704-10021 |  | CSR AREA | HO-242042 | 2062 | 2025-02-15 | HO-263011 | 1008 | 2025-06-28
SYS1-FCU8 | 15331704-10005 |  | SERVICE DEPT. (SIR ADOLF) | HO-242046 | 2062 | 2025-02-15 | HO-263014 | 1008 | 2025-06-28
SYS1-FCU9 | 15331704-10020 |  | MONITORING (RECHILLA) | HO-242045 | 2062 | 2025-02-15 | HO-263013 | 1008 | 2025-06-28
SYS1-FCU10 | 15331704-10024 |  | GRAPHICS/MARKETING | HO-243075 | 2069 | 2025-03-01 | HO-277305 | 1062 | 2025-10-20
SYS1-FCU11 | 15331704-10004 |  | STUDIO / M.ROOM | HO-241028 | 2056 | 2025-02-06 | HO-263015 | 1008 | 2025-06-28
SYS1-FCU12 | 15361704-10002 |  | 2ND FLR -HALLWAY |  |  |  | HO-275549 | 1071 | 2025-10-14
SYS1-FCU13 | 15331704-10003 |  | PANTRY 1 | HO-240945 | 2056 | 2025-02-06 | HO-263023 | 1008 | 2025-06-28
SYS1-FCU14 | 15331704-10016 |  | PANTRY 2 | HO-240947 | 2056 | 2025-02-06 | HO-263025 | 1008 | 2025-06-28
AIR CURTAIN | 14032210-10126 |  | PANTRY AREA |  |  |  | HO-273737 | 1050 | 2025-09-20
AHU |  |  | PANTRY -CANOPY |  |  |  | HO-275548 | 1062 | 2025-10-21
|  |  | 16 | 13 |  |  | 16
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
FCU 09 | 18071705-14420 | 3RD FLOOR | MIS SERVER ROOM 1 |  |  |  | HO-269065 | 1037 | 2025-09-06
FCU 10 | 18071705-14428 |  | MIS SERVER ROOM 2 |  |  |  | HO-269064 | 1037 | 2025-09-06
SYS2-FCU 07 | 15331704-10022 |  | ACCOUNTING SECTION |  |  |  | HO-268497 | 1030 | 2025-08-23
SYS2-FCU 08 | 15361704-10007 |  | 3RD FLR- HALL WAY-XEROX |  |  |  | HO-277869 | 1079 | 2025-11-15
SYS2-FCU 09 | 15321704-10001 |  | PAYROLL SECTION | HO-238669 | 2050 | 2025-01-25 | HO-269066 | 1033 | 2025-08-30
SYS2-FCU 10 | 15331704-10015 |  | TREASURY (MS. EDITH) |  |  |  | HO-270532 | 1033 | 2025-08-30
SYS2-FCU 11 | 15331704-10004 |  | CREDIT & COLLECTION | HO-243686 | 2069 | 2025-03-01 | HO-270443 | 1033 | 2025-08-30
SYS2-FCU 12 | 15361704-10003 |  | 3RD FLR- MALE CR |  |  |  | HO-282805 | 1113 | 2025-12-13
SYS2-FCU 13 | 15331704-10014 |  | SVC ACCOUNTING | HO-240293 | 2053 | 2025-02-01 | HO-250068 | 2086 | 2025-04-12
SYS2-FCU 14 | 15351704-10001 |  | TYT OFFICE | HO-243684 | 2069 | 2025-03-01 | HO-279741 | 1086 | 2025-11-13
SYS2-FCU 15 | 15331704-10009 |  | CONFERENCE ROOM | HO-250069 | 2086 | 2025-04-12 | HO-278684 | 1082 | 2025-10-29
SYS2-FCU 16 | 15331704-10013 |  | SOC.MED/ TELE-SURVEY |  |  |  | HO-268500 | 1030 | 2025-08-23
SYS2-FCU 17 | 15351704-10002 |  | MEETING ROOM |  |  |  | HO-268495 | 1030 | 2025-08-23
SYS2-FCU 18 | 15351704-10003 |  | OMF OFFICE |  |  |  | HO-268041 | 1025 | 2025-08-07
SYS2-FCU 19 | 15331704-10023 |  | ADMIN AND AUDIT DEPT. | HO-240291 | 2053 | 2025-02-01 | HO-279751 | 1086 | 2025-11-15
SYS2-FCU 20 | 15361704-10006 |  | 3RD FLR-FRONT ELEVATOR |  |  |  | HO-277874 | 1079 | 2025-11-15
SYS2-FCU 21 | 15331704-10017 |  | MIS DEPARTMENT | HO-240292 | 2053 | 2025-02-01 | HO-279752 | 1086 | 2025-11-15
AHU |  |  | FINANCE - SIR WILLY |  |  |  | HO-281668 | 1101 | 2025-11-27
|  |  | 18 | 7 |  |  | 17
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS2-FCU1 | 15361704-10004 | 4TH FLOOR | 4TH FLR - MALE CR |  |  |  | HO-275935 | 1076 | 2025-10-23 | W/o breaker
SYS2-FCU2 | 15331704-10019 |  | BOARD ROOM - ECY |  |  |  | HO-214997 | 1037 | 2025-09-07
SYS2-FCU3 | 15331704-10012 |  | EXECUTIVE ROOM |  |  |  | HO-275930 | 1074 | 2025-10-16
SYS2-FCU4 | 15361704-10005 |  | 4TH FLR - FRONT ELEVATOR |  |  |  | HO-275934 | 1070 | 2025-10-13
SYS2-FCU5 | 15331704-10018 |  | AVR 1 | HO-248042 | 2081 | 2025-03-29 | HO-273306 | 1044 | 2025-09-17
SYS2-FCU6 | 15331704-10006 |  | AVR 2 | HO-248053 | 2081 | 2025-03-29 | HO-273307 | 1044 | 2025-09-17
FCU 1 | 20131706-10017 |  | HR (MS. AMY)
FCU 2 | KLM-SS70-2C1M |  | NEW HR DEPT |  |  |  | HO-278685 | 1086 | 2025-11-15
FCU 3 | 20131706-10065 |  | RND OFFICE | HO-240294 | 2056 | 2025-02-06 | HO-281666 | 1105 | 2025-12-06
FCU 4 | 20131706-10064 |  | MUSEUM 1
FCU 5 | 20131708-10083 |  | MUSEUM 2
FCU7 | 17151806-10316 |  | AVR3-BACK SYS2 FCU5 | HO-248050 | 2081 | 2025-03-29 | HO-273305 | 1044 | 2025-09-17
FCU8 | 17151806-10341 |  | AVR4-BACK SYS2 FCU6 | HO-248049 | 2081 | 2025-03-29 | HO-273304 | 1044 | 2025-09-17
TRAINING ROOM | 18572203-11437 |  | TRAINING ROOM | HO-263551 | 1009 | 2025-07-03 | HO-278682 | 1081 | 2025-10-29
FCU 6 | 20121708-10077 |  | ADMIN STORAGE |  |  |  | HO-281670 | 1105 | 2025-12-06
AHU |  |  | MS. AMY AREA |  |  |  | HO-281667 | 1113 | 2025-12-13
|  |  | 16 | 6 |  |  | 13
|  |  | TOTAL AC - 1ST GC | 40 |  | 2ND-GC | 64
|  |  | TOTAL AC / AIR CURTAIN/ AHU | 68 |  |  | 68
|  |  |  | 58.82% |  |  | 94.12%

## AC Monitoring - GC- 2026
KOLIN PHILIPPINES INTERNATIONAL INC.
1854 Santa Rita St. Guadalupe Nuevo, Makati City
ACU/AHU PREVENTIVE MAINTENANCE SCHEDULE 2026
|  |  |  | 1st General Cleaning JAN - JUNE |  |  | 2nd General Cleaning JULY - DECEMBER
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS-ACU1(M) | 15401704-10006 | ROOF DECK | ROOF DECK | HO-285603 | 1118 | 2026-01-03
SYS-ACU1A | 15401704-10001 |  | ROOF DECK | HO-285593 | 1118 | 2026-01-03
SYS-ACU1B | 15401704-10005 |  | ROOF DECK | HO-285594 | 1118 | 2026-01-03
SYS-ACU1C | 15401704-10008 |  | ROOF DECK | HO-285591 | 1118 | 2026-01-03
SYS-ACU2(M) | 15401704-10007 |  | ROOF DECK | HO-285603 | 1118 | 2026-01-03
SYS-ACU2A | 15401704-10002 |  | ROOF DECK | HO-285599 | 1118 | 2026-01-03
SYS-ACU2B | 15401704-10004 |  | ROOF DECK | HO-285598 | 1118 | 2026-01-03
SYS-ACU2C | 15401704-10003 |  | ROOF DECK | HO-285597 | 1118 | 2026-01-03
AHU | 15411711-10001 |  | ROOF DECK | HO-285706 | 1118 | 2026-01-03
|  |  | 9 | 9 |  |  | 1
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS1-FCU15 | 15371704-10001 | UPPER GROUND | CLINIC | HO-289453 | 1128 | 2026-02-03
FCU11 | 18071705-14341 |  | TOOLS & PARTS OFFICE
FCU12 | 17151706-10195 |  | CUSTOMER LOUNGE
SYS1-FCU16 | 15331704-10011 |  | LOBBY AREA
SYS1-FCU17 | 15381704-10001 |  | SHOWROOM -HALLWAY | HO-285911 | 1128 | 2026-02-03
SYS1-FCU18 | 15381704-10002 |  | SHOWROOM - LEFT SIDE | HO-289512 | 1128 | 2026-02-03
AIR CURTAIN | 14032210-10023 |  | Reception - Right Side
| 14032210-10047 |  | Reception - Left Side
AHU |  |  | (UPPER GROUND) - Tech CR
|  |  | 9 | 3 |  |  | 0
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS1-FCU1 | 15331704-10010 | 2ND FLOOR | SALES DEPT | HO-288172 | 1124 | 2026-01-31
SYS1-FCU2 | 15331704-10001 |  | SALES DEPT. (MISS MITCH) | HO-288175 | 1124 | 2026-01-31
SYS1-FCU3 | 15341704-10001 |  | SALES DEPT. (SIR KEITH)
SYS1-FCU4 | 15361704-10001 |  | SALES DEPT. (MS. JOANA) | HO-288177 | 1124 | 2026-01-31
SYS1-FCU5 | 15331704-10008 |  | ACCOUNT OFFICERS | HO-288178 | 1124 | 2026-01-31
SYS1-FCU6 | 15331704-10007 |  | CSR AREA | HO-287822 | 1124 | 2026-01-31
SYS1-FCU7 | 15331704-10021 |  | CSR AREA | HO-287824 | 1124 | 2026-01-31
SYS1-FCU8 | 15331704-10005 |  | SERVICE DEPT. (SIR ADOLF) | HO-286700 | 1122 | 2026-01-17
SYS1-FCU9 | 15331704-10020 |  | MONITORING (RECHILLA) | HO-286701 | 1122 | 2026-01-17
SYS1-FCU10 | 15331704-10024 |  | GRAPHICS/MARKETING | HO-288169 | 1124 | 2026-01-31
SYS1-FCU11 | 15331704-10004 |  | STUDIO / M.ROOM | HO-288167 | 1124 | 2026-01-31
SYS1-FCU12 | 15361704-10002 |  | 2ND FLR -HALLWAY
SYS1-FCU13 | 15331704-10003 |  | PANTRY 1 | HO-286311 | 1121 | 2026-01-10
SYS1-FCU14 | 15331704-10016 |  | PANTRY 2 | HO-286312 | 1121 | 2026-01-10
AIR CURTAIN | 14032210-10126 |  | PANTRY AREA | HO-286313 | 1121 | 2026-01-10
AHU |  |  | PANTRY -CANOPY | HO-286315 | 1121 | 2026-01-10
|  |  | 16 | 14 |  |  | 0
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
FCU 09 | 18071705-14420 | 3RD FLOOR | MIS SERVER ROOM 1
FCU 10 | 18071705-14428 |  | MIS SERVER ROOM 2
SYS2-FCU 07 | 15331704-10022 |  | ACCOUNTING SECTION
SYS2-FCU 08 | 15361704-10007 |  | 3RD FLR- HALL WAY-XEROX
SYS2-FCU 09 | 15321704-10001 |  | PAYROLL SECTION
SYS2-FCU 10 | 15331704-10015 |  | TREASURY (MS. EDITH)
SYS2-FCU 11 | 15331704-10004 |  | CREDIT & COLLECTION
SYS2-FCU 12 | 15361704-10003 |  | 3RD FLR- MALE CR
SYS2-FCU 13 | 15331704-10014 |  | SVC ACCOUNTING
SYS2-FCU 14 | 15351704-10001 |  | TYT OFFICE
SYS2-FCU 15 | 15331704-10009 |  | CONFERENCE ROOM
SYS2-FCU 16 | 15331704-10013 |  | SOC.MED/ TELE-SURVEY
SYS2-FCU 17 | 15351704-10002 |  | MEETING ROOM
SYS2-FCU 18 | 15351704-10003 |  | OMF OFFICE
SYS2-FCU 19 | 15331704-10023 |  | ADMIN AND AUDIT DEPT.
SYS2-FCU 20 | 15361704-10006 |  | 3RD FLR-FRONT ELEVATOR
SYS2-FCU 21 | 15331704-10017 |  | MIS DEPARTMENT
AHU |  |  | FINANCE - SIR WILLY
|  |  | 18 | 0 |  |  | 0
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS2-FCU1 | 15361704-10004 | 4TH FLOOR | 4TH FLR - MALE CR
SYS2-FCU2 | 15331704-10019 |  | BOARD ROOM - ECY
SYS2-FCU3 | 15331704-10012 |  | EXECUTIVE ROOM
SYS2-FCU4 | 15361704-10005 |  | 4TH FLR - FRONT ELEVATOR
SYS2-FCU5 | 15331704-10018 |  | AVR 1
SYS2-FCU6 | 15331704-10006 |  | AVR 2
FCU 1 | 20131706-10017 |  | HR (MS. AMY)
FCU 2 | KLM-SS70-2C1M |  | NEW HR DEPT
FCU 3 | 20131706-10065 |  | RND OFFICE
FCU 4 | 20131706-10064 |  | MUSEUM 1
FCU 5 | 20131708-10083 |  | MUSEUM 2
FCU7 | 17151806-10316 |  | AVR3-BACK SYS2 FCU5
FCU8 | 17151806-10341 |  | AVR4-BACK SYS2 FCU6
TRAINING ROOM | 18572203-11437 |  | TRAINING ROOM
FCU 6 | 20121708-10077 |  | ADMIN STORAGE
AHU |  |  | MS. AMY AREA | HO-286698 | 1121 | 2026-01-17
|  |  | 16 | 1 |  |  | 0
|  |  | TOTAL AC - 1ST GC | 27 |  | 2ND-GC | 1
|  |  | TOTAL AC / AIR CURTAIN/ AHU | 68 |  |  | 68
|  |  |  | 39.71% |  |  | 1.471%

## UG - Repair
KOLIN PHILIPPINES INTERNATIONAL INC.
1854 Santa Rita St. Guadalupe Nuevo, Makati City
ACU/AHU PREVENTIVE MAINTENANCE SCHEDULE 2025
DATE | UNIT | LOCATION | SJR NO. | BWOR NO. | FINDINGS | REPAIR DONE | REMARKS
2025-07-15 | SYS1-FCU 16 | Lobby Area | HO-264616 | # 1014 | L3 / Deffective drain pump | Replaced drain pump | DONE-OK | KAC-48TCRM
2025-09-27 | KAC-36TCRM | Reception area | HO-274261 | # 1054 | Noisy Fan Motor | Replaced Fan motor | DONE-OK | KAC-36TCRM
2025-10-09 | KAC-36TCRM | Reception area 1 | HO-276293 | - | Noisy | Check up / wrong mounting of blower wheel | DONE-OK | FCU 12
2025-10-10 | KAC-36TCRM | Reception area 1 | HO-276304 | #1068 | Noisy | Corrected mounting of blower wheel 2 pcs | DONE-OK | SYS1-FCU 15
2025-10-10 | KAC-36TCRM | Reception area 2 | HO-275877 | #1068 | Noisy | Returned old fan motor / corrected mounting of blower wheel 3 pcs | DONE-OK | SYS1-FCU 16
SYS1-FCU 17
SYS1-FCU 18

## 2nd Flr - Repair
KOLIN PHILIPPINES INTERNATIONAL INC.
1854 Santa Rita St. Guadalupe Nuevo, Makati City
ACU/AHU PREVENTIVE MAINTENANCE SCHEDULE 2025
DATE | UNIT | LOCATION | SJR NO. | BWOR NO. | FINDINGS | REPAIR DONE | REMARKS
2025-02-08 | SYS1-FCU 2 | Ms. Mitch | HO-241270 | # 2060 | L3 Error / need Circuit breaker | Check up only | DONE-OK | KAC-36TCRM
2025-02-22 | SYS1-FCU 1 | Sales Dept. | HO-241444 | # 2066 | Others | Install Circuit breaker | DONE-OK | SYS1-FCU 1
2025-02-22 | SYS1-FCU 10 | Marketing | HO-242887 | # 2066 | Others | Install Circuit breaker | DONE-OK | SYS1-FCU 2
2025-02-22 | SYS1-FCU 2 | Ms. Mitch | HO-243008 | # 2066 | Others | Install Circuit breaker | DONE-OK | SYS1-FCU 3
2025-02-22 | SYS1-FCU 5 | Account officer | HO-241452 | # 2066 | Others | Install Circuit breaker | DONE-OK | SYS1-FCU 4
2025-03-01 | SYS1-FCU 4 | Ms. Joana | HO-263020 | # 2069 | Others | Install Circuit breaker | DONE-OK | SYS1-FCU 5
2025-03-10 | SYS1-FCU 6 | CSR Area | HO-244963 | # 2071 | H2 / PO Error/ Deffective PCB (odu) | Replaced PCB Outdoor | DONE-OK | SYS1-FCU 6
2025-04-30 | SYS1-FCU 2 | Ms. Mitch | HO-252961 | # 2088 | L3 Error /Deffective drain pump | Replaced Drain pump | DONE-OK | SYS1-FCU 7
2025-08-05 | SYS1-FCU 8 | Sir Adolf | HO-267957 | # 1021 | Check up only | Transfer Master Indoor from Sir Alvin to Sir adolff | DONE-OK | SYS1-FCU 8
2025-08-19 | SYS1-FCU 3 | Sir Keith | HO-269848 | # 1031 | Weak cooling | Re connect of connector | DONE-OK | SYS1-FCU 9
2025-08-26 | SYS1-FCU 3 | Sir Keith | HO-270389 | # 1031 | Weak cooling | Re connect of connector | DONE-OK | SYS1-FCU 10
2025-09-03 | SYS1-FCU 9 | Monitoring Area | HO-271676 | # 1035 | Water Dripping | Fixed Hose @ drain pump | DONE-OK | SYS1-FCU 11
2025-09-08 | SYS1-FCU 3 | Sir Keith | HO-271839 | # 1039 | Weak cooling | Reconnect temp sensor socket | DONE-OK | SYS1-FCU 12
2025-09-13 | SYS1-FCU 7 | CSR Area | HO-272904 | # 1043 | L3 Error | Reset socket connector | DONE-OK | SYS1-FCU 13
2025-09-27 | SYS1-FCU 7 | CSR Area | HO-274204 | # 1054 | Deffective water pump /clogged chain hose | Replaced water pump / drain hose | DONE-OK | SYS1-FCU 14

## 3rd Flr - Repair
KOLIN PHILIPPINES INTERNATIONAL INC.
1854 Santa Rita St. Guadalupe Nuevo, Makati City
ACU/AHU PREVENTIVE MAINTENANCE SCHEDULE 2025
DATE | UNIT | LOCATION | SJR NO. | BWOR NO. | FINDINGS | REPAIR DONE | REMARKS
2025-01-24 | SYS2-FCU 16 | SOCMED / TLSVEY | HO-239365 | # 2063 | L3 | Cleaning of Drain pump /water level switch | DONE-OK | FCU 9
2025-02-03 | SYS2-FCU 18 | OMF Office | HO-240603 | - | Water dripping | Remove slime from drain pump and drain pan adn put cable tie to support drain pan to prevent water stock | DONE-OK | FCU 10
2025-02-15 | SYS2-FCU 15 | Conference Room | HO-242188 | # 2062 | L3 / Deffective water pump | Replaced water pump | DONE-OK | SYS2-FCU 7
2025-02-17 | SYS2-FCU 18 | OMF Office | HO-242321 | # 2063 | Weak Cooling | Check parameters / Adjusted remote setting of another unit from dry mode to cool mode | DONE-OK | SYS2-FCU 8
2025-03-25 | SYS2-FCU 18 | OMF Office | HO-247333 | # 2078 | Weak Cooling | Replaced Temp sensor parts from small office | DONE-OK | SYS2-FCU 9
2025-03-26 | SYS2-FCU 18 | OMF Office | HO-247590 | # 2079 | Weak Cooling /L3 | Replaced water pump / water level switch | DONE-OK | SYS2-FCU 10
2025-03-29 | SYS2-FCU 11 | Credit /Collection | HO-248133 | # 2081 | Foul Odor | Removed anti bacterial filter /wash filter | DONE-OK | SYS2-FCU 11
2025-03-29 | SYS2-FCU 13 | SVC Accounting | HO-248132 | # 2081 | Foul Odor | Removed anti bacterial filter /wash filter | DONE-OK | SYS2-FCU 12
2025-04-30 | SYS2-FCU 17 | SOCMED / TLSVEY | HO-253284 | # 2088 | Water dripping | Clean drain pump only | DONE-OK | SYS2-FCU 13
2025-05-20 | SYS2-FCU 17 | SOCMED / TLSVEY | HO-256616 | # 2096 | L3 error code | Replaced water pump | DONE-OK | SYS2-FCU 14
2025-05-22 | SYS2-FCU 20 | FRONT-ELEVATOR | HO-255799 | # 2095 | Water dripping | Check up unit / Make manhole (Admin) | DONE-OK | SYS2-FCU 15
2025-05-23 | SYS2-FCU 18 | SOCMED / TLSVEY | HO-257479 | # 2096 | L3 error code | Replaced Drain pump hose | DONE-OK | SYS2-FCU 16
2025-05-31 | SYS2-FCU 20 | FRONT-ELEVATOR | HO-257486 | # 2096 | Water dripping | Re-insulate indoor fittings | DONE-OK | SYS2-FCU 17
2025-06-09 | SYS2-FCU 7 | Accounting section | HO-260295 | # 1003 | Blinking of light | Reset breaker only | DONE-OK | SYS2-FCU 18
2025-07-18 | SYS2-FCU 7 | Accounting section | HO-265722 | # 1016 | Deadset / Incorrect remote setting | Adjustment of Remote setting | DONE-OK | SYS2-FCU 19
2025-07-18 | SYS2-FCU 9 | PAYROLL | HO-265714 | # 1016 | Deadset / Incorrect remote setting | Adjustment of Remote setting | DONE-OK | SYS2-FCU 20
2025-07-18 | SYS2-FCU 10 | Ms. Edith | HO-265716 | # 1016 | Deadset / Incorrect remote setting | Adjustment of Remote setting | DONE-OK | SYS2-FCU 21
2025-07-18 | SYS2-FCU 13 | SVC Accounting | HO-265717 | # 1016 | Deadset / Incorrect remote setting | Adjustment of Remote setting | DONE-OK
2025-07-18 | SYS2-FCU 16 | SOCMED / TLSVEY | HO-265526 | # 1016 | Water dripping | Re insulation of drain line | DONE-OK
2025-07-18 | SYS2-FCU 19 | AIS /ADMIN | HO-265715 | # 1016 | Deadset / Incorrect remote setting | Adjustment of Remote setting | DONE-OK
2025-08-05 | SYS2-FCU 18 | OMF Office | HO-267927 | # 1021 | Weak Cooling / Dead set | Replaced PCB outdoor | DONE-OK
2025-08-07 | SYS2-FCU 18 | OMF Office | HO-268041 | # 1025 | Weak Cooling | Put breaker at Indoor | DONE-OK
2025-09-30 | SYS2-FCU 16 | SOCMED / TLSVEY | HO-274782 | # 1056 | Water dripping | Flushing drain line ,fixed drain hose using silicon | DONE-OK
2025-10-11 | SYS2-FCU 11 | Credit /Collection | HO-274403 | # 1069 | E2 error code | Check up / observed unit | DONE-OK
2025-10-13 | SYS2-FCU 16 | SOCMED / TLSVEY | HO-276572 | # 1070 | Water dripping | Put tape and electrical tape, re align main hose | DONE-OK
2025-10-15 | SYS2-FCU 10 | MARKETING | HO-276794 | # 1073 | Weak Cooling / Noisy fan motor | Check up / for 2nd action-GC | DONE-OK
2025-10-20 | SYS2-FCU 10 | MARKETING | HO-277305 | # 1062 | Dirty unit /replace fan motor | General cleaning / Replace Fan Motor | DONE-OK
2025-12-06 | SYS2-FCU 11 | Credit /Collection | HO-283176 | # 1111 | Blinking of light display | Check up and reset unit | DONE-OK
2025-12-13 | SYS2-FCU 9 | PAYROLL | HO-284141 | # 1113 | L3 error code | Replaced water pump / Run test OK | DONE-OK

## 4th Flr - Repair
KOLIN PHILIPPINES INTERNATIONAL INC.
1854 Santa Rita St. Guadalupe Nuevo, Makati City
ACU/AHU PREVENTIVE MAINTENANCE SCHEDULE 2025
DATE | UNIT | LOCATION | SJR NO. | BWOR NO. | FINDINGS | REPAIR DONE | REMARKS
2025-01-28 | FCU 1 | Ms.AMY | HO-239939 | # 2051 | Weak cooling | Check up | DONE-OK | FCU 1
2025-01-28 | FCU 2 | NEW HR | HO-239942 | - | Water dripping | Replaced water pump ,clean drain pump | DONE-OK | FCU 2
2025-01-31 | FCU 1 | Ms.AMY | HO-240405 | - | malfunstion of low pressure switch /deffective discharge sensor | Replaced Discharge sensor by pass low pressure switch | DONE-OK | FCU 3
2025-05-13 | SYS2-FCU 2 | BOARD ROOM | HO-259070 | # 2100 | Auto on & off / L3 error | Replaced fan motor | DONE-OK | FCU 4
2025-05-15 | FCU 3 | RND OFFICE | HO-255658 | # 2093 | Moisture copper tube | Put stickless and Aerotape | DONE-OK | FCU 5
2025-05-26 | FCU 1 | Ms.AMY | HO-257869 | # 2099 | Water dripping | Clean drain pad and pump | DONE-OK | FCU 6
2025-06-21 | FCU 1 | Ms.AMY | HO-261823 | # 1005 | Water dripping | Check up only / No trouble found | DONE-OK | FCU 7
2025-08-06 | SYS2-FCU 2 | BOARD ROOM | HO-268266 | # 1021 | Others | Transfer Master indoor from OMF to Board room | DONE-OK | FCU 8
2025-08-11 | FCU 1 | Ms.AMY | HO-268588 | # 1027 | Water dripping / Deffective compressor | Check up | DONE-OK | SYS2-FCU 1
2025-08-12 | FCU 1 | Ms.AMY | HO-268700 | # 1027 | Not cooling | Replaced Compressor / PCB outdoor | DONE-OK | SYS2-FCU 2
2025-10-08 | FCU 1 | Ms.AMY | HO-275960 | # 1066 | Water dripping | Re align unit/ replaced water pump / float switch | DONE-OK | SYS2-FCU 3
2025-10-11 | FCU 1 | Ms.AMY | HO-276542 | # 1069 | Water dripping | Check up / Removed water and drain pan | DONE-OK | SYS2-FCU 4
2025-10-25 | FCU 1 | Ms.AMY | HO-277306 | #1060 | Flushing chain line | replaced board and install circuit breaker | DONE-OK | SYS2-FCU 5
SYS2-FCU 6
HR TRAINING ROOM

## FOR PRINT (hidden)
KOLIN PHILIPPINES INTERNATIONAL INC.
1854 Santa Rita St. Guadalupe Nuevo, Makati City
ACU/AHU PREVENTIVE MAINTENANCE SCHEDULE 2025
|  |  |  | 1st General Cleaning JAN - JUNE |  |  | 2nd General Cleaning JULY - DECEMBER
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS-ACU1(M) | 15401704-10006 | ROOF DECK | ROOF DECK | HO-237287 | 2044 | 2025-01-11 | HO-272849 | 1043 | 2025-09-13
SYS-ACU1A | 15401704-10001 |  | ROOF DECK | HO-237275 | 2044 | 2025-01-11 | HO-272848 | 1043 | 2025-09-13
SYS-ACU1B | 15401704-10005 |  | ROOF DECK | HO-237277 | 2044 | 2025-01-11 | HO-272846 | 1043 | 2025-09-13
SYS-ACU1C | 15401704-10008 |  | ROOF DECK | HO-237274 | 2044 | 2025-01-11 | HO-272844 | 1043 | 2025-09-13
SYS-ACU2(M) | 15401704-10007 |  | ROOF DECK | HO-237279 | 2044 | 2025-01-11 | HO-272854 | 1043 | 2025-09-13
SYS-ACU2A | 15401704-10002 |  | ROOF DECK | HO-237285 | 2044 | 2025-01-11 | HO-272853 | 1043 | 2025-09-13
SYS-ACU2B | 15401704-10004 |  | ROOF DECK | HO-237283 | 2044 | 2025-01-11 | HO-272852 | 1043 | 2025-09-13
SYS-ACU2C | 15401704-10003 |  | ROOF DECK | HO-237280 | 2044 | 2025-01-11 | HO-272850 | 1043 | 2025-09-13
AHU | 15411711-10001 |  | ROOF DECK | HO-237278 | 2044 | 2025-01-11 | HO-272855 | 1043 | 2025-09-13
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS1-FCU15 | 15371704-10001 | UPPER GROUND | CLINIC |  |  |  | HO-273318 | 1045 | 2025-09-20
FCU11 | 18071705-14341 |  | TOOLS & PARTS OFFICE | HO-237958 | 2048 | 2025-01-18 | HO-273243 | 1050 | 2025-09-20
FCU12 | 17151706-10195 |  | CUSTOMER LOUNGE | HO-237957 | 2050 | 2025-01-25 | HO-273244 | 1050 | 2025-09-20
SYS1-FCU16 | 15331704-10011 |  | LOBBY AREA | HO-239122 | 2050 | 2025-01-25 | HO-264616 | 1014 | 2025-07-12
SYS1-FCU17 | 15381704-10001 |  | SHOWROOM -HALLWAY | HO-237962 | 2047 | 2025-01-15
SYS1-FCU18 | 15381704-10002 |  | SHOWROOM - LEFT SIDE | HO-237961 | 2047 | 2025-01-15
AIR CURTAIN | 14032210-10023 |  | Reception - Right Side |  |  |  | HO-273734 | 1050 | 2025-09-20
| 14032210-10047 |  | Reception - Left Side |  |  |  | HO-273736 | 1050 | 2025-09-20
AHU |  |  | (UPPER GROUND) - Tech CR
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS1-FCU1 | 15331704-10010 | 2ND FLOOR | SALES DEPT | HO-240949 | 2060 | 2025-02-08
SYS1-FCU2 | 15331704-10001 |  | SALES DEPT. (MISS MITCH) | HO-241270 | 2066 | 2025-02-08
SYS1-FCU3 | 15341704-10001 |  | SALES DEPT. (SIR KEITH) | HO-237273 | 2044 | 2025-01-11 | HO-267268 | 1025 | 2025-08-07
SYS1-FCU4 | 15361704-10001 |  | SALES DEPT. (MS. JOANA) | HO-241271 | 2060 | 2025-02-08 | HO-263020 | 1014 | 2025-07-12
SYS1-FCU5 | 15331704-10008 |  | ACCOUNT OFFICERS | HO-241274 | 2060 | 2025-02-08 | HO-263019 | 1014 | 2025-07-12
SYS1-FCU6 | 15331704-10007 |  | CSR AREA | HO-242044 | 2062 | 2025-02-15 | HO-263012 | 1008 | 2025-06-28
SYS1-FCU7 | 15331704-10021 |  | CSR AREA | HO-242042 | 2062 | 2025-02-15 | HO-263011 | 1008 | 2025-06-28
SYS1-FCU8 | 15331704-10005 |  | SERVICE DEPT. (SIR ADOLF) | HO-242046 | 2062 | 2025-02-15 | HO-263014 | 1008 | 2025-06-28
SYS1-FCU9 | 15331704-10020 |  | MONITORING (RECHILLA) | HO-242045 | 2062 | 2025-02-15 | HO-263013 | 1008 | 2025-06-28
SYS1-FCU10 | 15331704-10024 |  | GRAPHICS/MARKETING | HO-243075 | 2069 | 2025-03-01 | HO-263017 | 1008 | 2025-06-28
SYS1-FCU11 | 15331704-10004 |  | STUDIO / M.ROOM | HO-241028 | 2056 | 2025-02-06 | HO-263015 | 1008 | 2025-06-28
SYS1-FCU12 | 15361704-10002 |  | 2ND FLR -HALLWAY
SYS1-FCU13 | 15331704-10003 |  | PANTRY 1 | HO-240945 | 2056 | 2025-02-06 | HO-263023 | 1008 | 2025-06-28
SYS1-FCU14 | 15331704-10016 |  | PANTRY 2 | HO-240947 | 2056 | 2025-02-06 | HO-263025 | 1008 | 2025-06-28
AIR CURTAIN | 14032210-10126 |  | PANTRY AREA |  |  |  | HO-273737 | 1050 | 2025-09-20
AHU |  |  | PANTRY -CANOPY
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
FCU 09 | 18071705-14420 | 3RD FLOOR | MIS SERVER ROOM 1 |  |  |  | HO-269065 | 1037 | 2025-09-06
FCU 10 | 18071705-14428 |  | MIS SERVER ROOM 2 |  |  |  | HO-269064 | 1037 | 2025-09-06
SYS2-FCU 07 | 15331704-10022 |  | ACCOUNTING SECTION |  |  |  | HO-268497 | 1030 | 2025-08-23
SYS2-FCU 08 | 15361704-10007 |  | 3RD FLR- HALL WAY-XEROX
SYS2-FCU 09 | 15321704-10001 |  | PAYROLL SECTION | HO-238669 | 2050 | 2025-01-25 | HO-269066 | 1033 | 2025-08-30
SYS2-FCU 10 | 15331704-10015 |  | TREASURY (MS. EDITH) |  |  |  | HO-270532 | 1033 | 2025-08-30
SYS2-FCU 11 | 15331704-10004 |  | CREDIT & COLLECTION | HO-243686 | 2069 | 2025-03-01 | HO-270443 | 1033 | 2025-08-30
SYS2-FCU 12 | 15361704-10003 |  | 3RD FLR- MALE CR
SYS2-FCU 13 | 15331704-10014 |  | SVC ACCOUNTING | HO-240293 | 2053 | 2025-02-01 | HO-250068 | 2086 | 2025-04-12
SYS2-FCU 14 | 15351704-10001 |  | TYT OFFICE | HO-243684 | 2069 | 2025-03-01
SYS2-FCU 15 | 15331704-10009 |  | CONFERENCE ROOM | HO-250069 | 2086 | 2025-04-12
SYS2-FCU 16 | 15331704-10013 |  | SOC.MED/ TELE-SURVEY |  |  |  | HO-268500 | 1030 | 2025-08-23
SYS2-FCU 17 | 15351704-10002 |  | MEETING ROOM |  |  |  | HO-268495 | 1030 | 2025-08-23
SYS2-FCU 18 | 15351704-10003 |  | OMF OFFICE |  |  |  | HO-268041 | 1025 | 2025-08-07
SYS2-FCU 19 | 15331704-10023 |  | ADMIN AND AUDIT DEPT. | HO-240291 | 2053 | 2025-02-01
SYS2-FCU 20 | 15361704-10006 |  | 3RD FLR-FRONT ELEVATOR
SYS2-FCU 21 | 15331704-10017 |  | MIS DEPARTMENT | HO-240292 | 2053 | 2025-02-01
AHU |  |  | FINANCE - SIR WILLY
UNIT | SERIAL NUMBER | AREA | LOCATION | S.J.R No: | B.W.O.R | Date-Done | S.J.R No: | B.W.O.R | Date-Done
SYS2-FCU1 | 15361704-10004 | 4TH FLOOR | 4TH FLR - MALE CR
SYS2-FCU2 | 15331704-10019 |  | BOARD ROOM - ECY |  |  |  | HO-214997 | 1037 | 2025-09-07
SYS2-FCU3 | 15331704-10012 |  | EXECUTIVE ROOM
SYS2-FCU4 | 15361704-10005 |  | 4TH FLR - FRONT ELEVATOR
SYS2-FCU5 | 15331704-10018 |  | AVR 1 | HO-248042 | 2081 | 2025-03-29 | HO-273306 | 1044 | 2025-09-17
SYS2-FCU6 | 15331704-10006 |  | AVR 2 | HO-248053 | 2081 | 2025-03-29 | HO-273307 | 1044 | 2025-09-17
FCU 1 | 20131706-10017 |  | HR (MS. AMY)
FCU 2 | KLM-SS70-2C1M |  | NEW HR DEPT
FCU 3 | 20131706-10065 |  | RND OFFICE | HO-240294 | 2056 | 2025-02-06
FCU 4 | 20131706-10064 |  | MUSEUM 1
FCU 5 | 20131708-10083 |  | MUSEUM 2
FCU7 | 17151806-10316 |  | AVR3-BACK SYS2 FCU5 | HO-248050 | 2081 | 2025-03-29 | HO-273305 | 1044 | 2025-09-17
FCU8 | 17151806-10341 |  | AVR4-BACK SYS2 FCU6 | HO-248049 | 2081 | 2025-03-29 | HO-273304 | 1044 | 2025-09-17
TRAINING ROOM | 18572203-11437 |  | TRAINING ROOM | HO-263551 | 1009 | 2025-07-03
FCU 6 | 20121708-10077 |  | ADMIN STORAGE
AHU |  |  | MS. AMY AREA