## Summary
ERROR CODE | SYS1 - ODU | SYS2 - ODU | SYS1 - INDOOR | SYS2 - INDOOR
E2 Error | 5
L3 Error |  |  | 6 | 6
PO & H2 Error code | 1 |  | 1
Water Dripping |  |  | 1 | 6
Weak Cooling |  |  | 1 | 4

## SYS1-outdoor
OUTDOOR UNIT | DATE | SJR NO. | FINDINGS | SCOPE OF WORK | REMARKS
SYS1-MASTER | 2025-01-11 | HO-237287 | Dirty unit | General cleaning of outdoor only | DONE -OK
SYS1-ACU 1A | 2025-01-11 | HO-237275 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS1-ACU 1B | 2025-01-11 | HO-237277 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS1-ACU 1C | 2025-01-11 | HO-237274 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS1-MASTER | 2025-03-11 | HO-245244 | For replacement of S. tape | Replaced S. tape | DONE -OK
SYS1-ACU 1A | 2025-03-11 | HO-245238 | For replacement of S. Tape | Replaced S. tape | DONE-OK
SYS1-ACU 1B | 2025-03-11 | HO-245239 | For replacement of S. Tape | Replaced S. tape | DONE-OK
SYS1-ACU 1C | 2025-03-11 | HO-245237 | For replacement of S. Tape | Replaced S. tape | DONE-OK
SYS1-ACU 1C | 2025-06-10 | HO-260604 | E2 Error | Replaced Ambient outdoor sensor / discharge sensor | DONE-OK
SYS1-ACU 1C | 2025-06-20 | HO-261981 | E2 Error | Replaced 1 set outdoor sensor | DONE-OK
SYS1-ACU 1C | 2025-06-23 | HO-262204 | E2 Error | Re set circuit breaker | DONE-OK
SYS1-ACU 1C | 2025-07-04 | HO-263245 | E2 Error | Replaced PCB outdoor | DONE-OK
SYS1-MASTER | 2025-09-13 | HO-272849 | Dirty unit | General cleaning of outdoor only | DONE -OK
SYS1-ACU 1A | 2025-09-13 | HO-272848 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS1-ACU 1B | 2025-09-13 | HO-272846 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS1-MASTER | 2025-10-11 | HO-274405 | E2 Error | Check up / test and observed unit | DONE -OK
SYS1-ACU 1A | 1028-25 | HO-278492 | Error PO and H2 (Indoor) Error P3 , HL , C3 , C2 (outdoor) Deffective compressor drive board and fan motor drive board ( from 8:00 am to 6:35 pm) | Replaced compressor drive board, Cleaned and resoldered fan motor drive board by Sir Angel. | DONE -OK

## SYS1-Indoor
INDOOR UNIT | LOCATION | AREA | DATE | SJR NO. | FINDINGS | SCOPE OF WORK | REMARKS
SYS1-FCU 3 | 2ND | Sir Keith | 2025-01-11 | HO-237273 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 17 | UG | Showroom-Hallway | 2025-01-16 | HO-237962 | Dirty unit | General cleaning only - 1st | DONE-OK
SYS1-FCU18 | UG | Showroom-Left side | 2025-01-16 | HO-237961 | Dirty unit | General cleaning only - 1st | DONE-OK
SYS1-FCU16 | UG | LOBBY | 2025-01-25 | HO-239122 | Dirty unit | General cleaning only -1st | DONE -OK
SYS1-FCU 13 | 2ND | PANTRY 1 | 2025-02-06 | HO-240945 | Dirty unit | General cleaning only - 1ST | DONE-OK
SYS1-FCU 14 | 2ND | PANTRY 2 | 2025-02-06 | HO-240947 | Dirty unit | Ceneral cleaning only | DONE-OK
SYS1-FCU 1 | 2ND | Sir Andrew | 2025-02-08 | HO-240949 | Dirty unit | General cleaning only - 1st | DONE-OK
SYS1-FCU 2 | 2ND | Ms. Mitch | 2025-02-08 | HO-241270 | L3 Error / Dirty unit / Need Circuit breaker | Check up only | DONE-OK
SYS1-FCU 4 | 2ND | Sales | 2025-02-08 | HO-241271 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 5 | 2ND | account officer | 2025-02-08 | HO-241274 | Dirty unit | General cleaning only / Test run | DONE-OK
SYS1-FCU 6 | 2ND | CSR 1 | 2025-02-15 | HO-242044 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 7 | 2ND | CSR 2 | 2025-02-15 | HO-242042 | Dirty unit | General cleaning only -1ST | DONE-OK
SYS1-FCU 8 | 2ND | Sir Adolf | 2025-02-15 | HO-242046 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 9 | 2ND | Monitoring area | 2025-02-15 | HO-242045 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 1 | 2ND | Sir Andrew | 2025-02-22 | HO-241444 | No circuit breaker | Install circuit breaker | DONE-OK
SYS1-FCU 2 | 2ND | Ms. Mitch | 2025-02-22 | HO-243008 | L3 Error | Install Circuit breaker / Test Run | DONE-OK
SYS1-FCU 5 | 2ND | account officer | 2025-02-22 | HO-241452 | No circuit breaker | Installation of Circuit breaker / Test run | DONE-OK
SYS1-FCU 10 | 2ND | Marketing | 2025-02-22 | HO-242887 | No ciccuit breaker | Installation of Circuit breaker | DONE-OK
SYS1-FCU 4 | 2ND | Sales | 2025-03-01 | HO-241446 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 10 | 2ND | Marketing | 2025-03-01 | HO-243075 | Dirty unit | General cleaning only - 1ST | DONE-OK
SYS1-FCU 6 | 2ND | CSR 1 | 2025-03-10 | HO-244963 | PO & H2 Error code | Replaced PCB outdpor | DONE-OK
SYS1-FCU 2 | 2ND | Ms. Mitch | 2025-04-28 | HO-252961 | L3 Error /Deffective drain pump | Replaced Drain Pump | DONE-OK
SYS1-FCU 11 | 2ND | Meeting room | 2025-05-06 | HO-241028 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 6 | 2ND | CSR 1 | 2025-06-28 | HO-263012 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 7 | 2ND | CSR 2 | 2025-06-28 | HO-263011 | Dirty unit | General cleaning only - 2ND | DONE-OK
SYS1-FCU 8 | 2ND | Sir Adolf | 2025-06-28 | HO-263014 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 9 | 2ND | Monitoring area | 2025-06-28 | HO-263013 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 11 | 2ND | Meeting room | 2025-06-28 | HO-263015 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 13 | 2ND | PANTRY 1 | 2025-06-28 | HO-263023 | Dirty unit | General cleaning only - 2ND | DONE-OK
SYS1-FCU 14 | 2ND | PANTRY 2 | 2025-06-28 | HO-263025 | Dirty unit | Ceneral cleaning only | DONE-OK
SYS1-FCU16 | UG | LOBBY | 2025-07-12 | HO-264616 | Dirty unit / L3 Error | Replaced drain pump / 2nd GC | DONE-OK
SYS1-FCU 4 | 2ND | Sales | 2025-07-12 | HO-263020 | Dirty Filter | Clean filter only | DONE-OK
SYS1-FCU 5 | 2ND | account officer | 2025-07-12 | HO-263019 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 8 | 2ND | Sir Adolf | 2025-08-05 | HO-269757 | Check up | Transfer master indoor from Sir alvin to Sir Adolf | DONE-OK
SYS1-FCU 3 | 2ND | Sir Keith | 2025-08-07 | HO-267268 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 3 | 2ND | Sir Keith | 2025-08-19 | HO-269848 | Weak Cooling | Reconnect of connector | DONE-OK
SYS1-FCU 3 | 2ND | Sir Keith | 2025-08-26 | HO-270389 | Weak Cooling | Reconnect of connector | DONE-OK
SYS1-FCU 9 | 2ND | Monitoring area | 2025-09-03 | HO-271676 | Water dripping | Fixed hose & drain pump | DONE-OK
SYS1-FCU 3 | 2ND | Sir Keith | 2025-09-08 | HO-271839 | Weak Cooling | Reconnect of Temp sensor socket | DONE-OK
SYS1-FCU 7 | 2ND | CSR 2 | 2025-09-13 | HO-272904 | L3 Error | Reset socket connector | DONE-OK
SYS1-FCU15 | UG | CLINIC | 2025-09-20 | HO-273318 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 7 | 2ND | CSR 2 | 2025-09-20 | HO-273252 | L3 Error / repeat GC | General cleaning only | DONE-OK
SYS1-FCU 17 | UG | Showroom-Hallway | 2025-09-27 | HO-273980 | Dirty unit | Clean Filter only - 2nd | DONE-OK
SYS1-FCU18 | UG | Showroom-Left side | 2025-09-27 | HO-273982 | Dirty unit | Clean filter only | DONE-OK
SYS1-FCU 7 | 2ND | CSR 2 | 2025-09-27 | HO-274204 | Deffective water pump / clogged chain hose | Replaced water pump and drain hose | DONE-OK
SYS1-FCU 12 | 2ND | HALLWAY | 2025-09-27 | HO-274207 | Dirty unit | General cleaning only | DONE-OK
SYS1-FCU 17 | UG | Showroom-Hallway | 2025-10-02 | HO-275273 | Dirty unit | General cleaning only - 2nd | DONE-OK
SYS1-FCU18 | UG | Showroom-Left side | 2025-10-02 | HO-275273 | Dirty unit | General cleaning only -2ND | DONE-OK
SYS1-FCU 10 | 2ND | Marketing | 2025-10-20 | HO-277305 | Dirty unit / Replacement of Fan motor | General cleaning / replaced fan motor | DONE-OK
SYS1-FCU 1 | 2ND | Sir Andrew | 2025-10-25 | HO-277306 | Dirty unit | General cleaning only - 2nd | DONE-OK
SYS1-FCU 2 | 2ND | Ms. Mitch | 2025-10-25 | HO-275519 | Dirty unit | General cleaning only | DONE-OK

## SYS2-outdoor
OUTDOOR UNIT | DATE | SJR NO. | FINDINGS | SCOPE OF WORK | REMARKS
SYS2-MASTER | 2025-01-11 | HO-237279 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS2-ACU 2A | 2025-01-11 | HO-237285 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS2-ACU 2B | 2025-01-11 | HO-237283 | Dirty unit | General cleaning of outdoor only | DONE -OK
SYS2-ACU 2C | 2025-01-11 | HO-237280 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS2-MASTER | 2025-03-11 | HO-245241 | For replacement of S. tape | Replaced S. tape | DONE -OK
SYS2-ACU 2A | 2025-03-11 | HO-245245 | For replacement of S. Tape | Replaced S. tape | DONE-OK
SYS2-ACU 2B | 2025-03-11 | HO-245247 | For replacement of S. Tape | Replaced S. tape | DONE-OK
SYS2-ACU 2C | 2025-03-11 | HO-245243 | For replacement of S. Tape | Replaced S. tape | DONE-OK
SYS2-MASTER | 2025-09-13 | HO-272854 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS2-ACU 2A | 2025-09-13 | HO-272853 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS2-ACU 2B | 2025-09-13 | HO-272852 | Dirty unit | General cleaning of outdoor only | DONE-OK
SYS2-ACU 2C | 2025-09-13 | HO-272850 | Dirty unit | General cleaning of outdoor only | DONE-OK

## SYS2-Indoor
INDOOR UNIT | LOCATION | AREA | DATE | SJR NO. | FINDINGS | SCOPE OF WORK | REMARKS
SYS2-FCU 16 | 3RD | SOCMED /OOP | 2025-01-24 | HO-239365 | L3 Error | Cleaning of drain pump | DONE-OK
SYS2-FCU 9 | 3RD | PAYROLL | 2025-01-25 | HO-238669 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 19 | 3RD | ADMIN-AUDIT | 2025-02-01 | HO-240291 | Dirty unit | General cleaning only - 1st | DONE-OK
SYS2-FCU 21 | 3RD | MIS | 2025-02-01 | HO-240292 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 18 | 3RD | OMF OFFICE | 2025-02-03 | HO-240603 | WATER dripping | Remove slime from drain pump pan and put cable tie to support drain pan to prevent water stuck | DONE-OK
SYS2-FCU 15 | 3RD | CONFERENCE ROOM | 2025-02-15 | HO-242188 | L3 Error / Deffective power pump | Replaced water pump | DONE-OK
SYS2-FCU 18 | 3RD | OMF OFFICE | 2025-02-17 | HO-242321 | Weak cooling / Dry mode setting from another indoor | Check parameters /Adjusted remote setting from dry to cool mode | DONE-OK
SYS2-FCU 11 | 3RD | CREDIT & COLLECTION | 2025-03-01 | HO-243686 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 14 | 3RD | TYT OFFICE | 2025-03-01 | HO-243684 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 18 | 3RD | OMF OFFICE | 2025-03-24 | HO-247278 | Weak cooling | Endorse remote and remote holder | DONE-OK
SYS2-FCU 18 | 3RD | OMF OFFICE | 2025-03-25 | HO-247333 | Weak cooling | Reduced temp sensor | DONE-OK
SYS2-FCU 18 | 3RD | OMF OFFICE | 2025-03-26 | HO-247590 | L3 ERROR | Replaced water pump /water level switch | DONE-OK
SYS2-FCU 5 | 4TH | AVR 1 | 2025-03-29 | HO-248042 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 6 | 4TH | AVR 2 | 2025-03-29 | HO-248053 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 11 | 3RD | CREDIT & COLLECTION | 2025-03-29 | HO-248133 | Foul Odor | Removed anti bacterial filter /wash filter | DONE-OK
SYS2-FCU 13 | 3RD | SVC ACCOUNTING | 2025-03-29 | HO-248132 | Foul Odor | Removed anti bacterial filter and wash filter | DONE-OK
SYS2-FCU 13 | 3RD | SVC ACCOUNTING | 2025-04-12 | HO-250068 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 15 | 3RD | CONFERENCE ROOM | 2025-04-12 | HO-250069 | Dirty unit | General cleaning only- 1ST | DONE-OK
SYS2-FCU 16 | 3RD | SOCMED /OOP | 2025-04-30 | HO-253284 | Water dripping | Clean drain pump | DONE-OK
SYS2-FCU 2 | 4TH | BOARD ROOM | 2025-05-13 | HO-259070 | Auto on & off / L3 error | Replaced fan motor | DONE-OK
SYS2-FCU 16 | 3RD | SOCMED /OOP | 2025-05-20 | HO-256616 | L3 Error | Replaced water pump / Modification of drain line | DONE-OK
SYS2-FCU 16 | 3RD | SOCMED /OOP | 2025-05-22 | HO-257479 | L3 Error | Replaced drain pump | DONE-OK
SYS2-FCU 20 | 3RD | FRONT ELEVATOR | 2025-05-22 | HO-255799 | Water dripping | Check up only | DONE-OK
SYS2-FCU 20 | 3RD | FRONT ELEVATOR | 2025-05-31 | HO-257486 | Water dripping | Re insulate (I) fittings | DONE-OK
SYS2-FCU 7 | 3RD | ACCOUNTING | 2025-06-09 | HO-260295 | Blinking of light | Reset breaker only | DONE-OK
SYS2-FCU 7 | 3RD | ACCOUNTING | 2025-07-18 | HO-265722 | Dead Set | Adjustment of remote Setting | DONE-OK
SYS2-FCU 9 | 3RD | PAYROLL | 2025-07-18 | HO-265714 | Dead set | Adjustment of Remore setting | DONE-OK
SYS2-FCU 10 | 3RD | TREASURY | 2025-07-18 | HO-265716 | Deadset / Incorrect remote setting | Adjustment of Remote setting | DONE-OK
SYS2-FCU 13 | 3RD | SVC ACCOUNTING | 2025-07-18 | HO-265717 | Dead set | Adjustment of remote setting | DONE-OK
SYS2-FCU 16 | 3RD | SOCMED /OOP | 2025-07-18 | HO-265526 | Water dripping | Re insulation of drain line | DONE-OK
SYS2-FCU 19 | 3RD | ADMIN-AUDIT | 2025-07-18 | HO-265715 | Deadset / remote setting incorrect | Adjustment of setting on Remote | DONE-OK
SYS2-FCU 18 | 3RD | OMF OFFICE | 2025-08-05 | HO-267927 | Weak cooling | Replaced PCB Indoor | DONE-OK
SYS2-FCU 2 | 4TH | BOARD ROOM | 2025-08-06 | HO-268266 | Others | Transfer Master indoor from OMF to Board room | DONE-OK
SYS2-FCU 7 | 3RD | ACCOUNTING | 2025-08-23 | HO-268497 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 16 | 3RD | SOCMED /OOP | 2025-08-23 | HO-268500 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 17 | 3RD | MEETING ROOM | 2025-08-23 | HO-268495 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 9 | 3RD | PAYROLL | 2025-08-30 | HO-269065 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 10 | 3RD | TREASURY | 2025-08-30 | HO-270532 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 11 | 3RD | CREDIT & COLLECTION | 2025-08-30 | HO-270443 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 2 | 4TH | BOARD ROOM | 2025-09-07 | HO-214997 | Dirty unit | General cleaning only | DONE -OK
SYS2-FCU 5 | 4TH | AVR 1 | 2025-09-17 | HO-273306 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 6 | 4TH | AVR 2 | 2025-09-17 | HO-273307 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 16 | 3RD | SOCMED /OOP | 2025-09-29 | HO-274782 | Water dripping | Flushing drain line, fixed drain line hose, using silicon | DONE-OK
SYS2-FCU 4 | 4TH | FRONT ELEVATOR | 2025-10-13 | HO-75934 | Dirty unit | General cleaning only / Put breaker 20 amps | DONE-OK
SYS2-FCU 3 | 4TH | EXECUTIVE ROOM | 2025-10-16 | HO-275930 | Dirty unit | General cleaning only | DONE-OK
SYS2-FCU 1 | 4TH | HALLWAY-CR | 2025-10-23 | HO-275935 | Dirty unit | General cleaning only | DONE-OK